## Info
Header Information
TDSP | Operator of the Major Transmission Element.
Major Transmission Element (MTE) | Transmission Element which was, or scheduled to be, on outage and has been associated with one or more high congestion(s).
Equip. Type | Equipment Type of the MTE.
kV | Voltage Level of the MTE.
Congestion Year/Month | Year and Month the associated congestion occurred.
Contingency | Contingency associated with the MTE.
Overload | Overload associated with the MTE.
Source | Source of the information: RT = Based on historical Real-Time congestion, ST = Based on Outage Coordination Studies. ADD = Addition Requests (both Private and Public)
Outage Type | Outage Type is categorized to be either Planned (PL) and Forced (FR, FE, UE, M1, M2, M3)
Cancel | Outage(s) for the specific MTE was Cancelled, Rejected, or Withdrawn.
Removal Requestor | Stakeholder who is requesting to remove the MTE from the list (Organization)
Addition Requestor | Stakeholder who is requesting to add the MTE from the list (Organization)
Reason for Addition | Justification for adding the MTE to the list. Details of the specific scenarios that the MTE may cause high congestion, including but not limited to: 1. ERCOT Load Level: Peak, Off-Peak (or 35GW, 70GW, etc). 2. Any specific regional load condition: High Houston Load, etc. 3. Wind Generation Level: High, Mid, Low, or N/A. 4. Solar Geneartion Level: High, Mid, Low, or N/A. 5. Any specific abnormal transmission equipment status: i.e. 345 kV line from A to B out-of-service, etc. 6. For Private Submissions, any specific generator output level: i.e. Resource A at 300 MW or above, etc. 7. (Optional) PSSE or PowerWorld case if available.
Reason for Removal | Justification for removing the MTE from the list. Usually entails a Transmission Upgrade Project.
OCITF Consensus | Consensus after OCITF meetings.
Decision | Final (TAC) Decision of the Addition/Removal Request for Non-Consensus items.
Discussion Items | Any other information that stakeholder(s) want to discuss during the OCITF meetings.

## MTE(2018)
TDSP | Major Transmission Element (MTE) | Equip. Type | kV | Congestion Year/Month | Contingency | Overload | Source | Outage Type | Cancel | Removal Requestor | Reason for Removal | OCITF Consensus | Decision | Discussion Items
AEN | Hamilton Aen CB HM_950 | CB | 138 | 15/4 | DCKT Burleson to Carson Creek 138 kV & Pedernales to Advanced Micro Devices Aen 138 kV | Manesium Plant - Northlan 138 kV | RT | Forced
AEN | Howard Lane Aen - Techridge | LN | 138 | 17/1 | DCKT Austrop to Daffin Gin & Aen Dunlap to Decker 138 kV | Howard Lane Tap - Howard Lane Aen 138 kV | ST | Planned
AEN | Slaughter Lane - Lytton Springs | LN | 138 | 17/11 | DCKT Stoney Ridge to Garfield Aen & Hicross Aen to Garfield Aen 138 kV | Lytton Springs - Pilot Knob 138 kV | RT | Planned
AEN, LCRA | Holman Aen - Fayette Plant 2 | LN | 345 | 17/5 | DCKT Fayetteville Plant 1 to Fayetteville & Fayette Plant 1 to Salem 345 kV | Sam Gideon - Winchester 138 kV | RT | Planned
AEP | Agave - Lon Hill | LN | 138 | 17/8 | DCKT San Miguel Gen to Elmcreek 345 kV | Pawnee Switching Station - Calaveras 345 kV | RT | Forced
AEP | Air Liquide Ingleside - … - Dupont Sw - Ingleside & Oxychem Ingleside | LN | 138 | 16/4, 17/8, 18/1 | Dupont Pp1 Ingleside to Ingleside Cogen Sw 138 kV (3A), Lon Hill to Coleto Creek 345 kV, Dupont Sw - Ingleside to Ingleside Cogen Sw 138 Kv | Duppont Pp1 Ingleside - Duppont Sw Ingleside 138 kV, Lon Hill - Pawnee Switching Station 345 kV, Dupont Pp1 - Ingleside to Dupont Sw - Ingleside 138 kV | ST, RT | Planned, Forced
AEP | Airco Aep - Rincon | LN | 138 | 17/5, 17/9, 17/10 | DCKT Victoria to Victoria Dupont Sw & Victoria Dupont Sw to Victoria 138 kV, Coleto Creek to Victoria 138 kV, DCKT Haisley to Warburton Road Switching Station 138 kV & Lon Hill to Coleto Creek 345 kV, Coleto Creek to Victoria 138 kV | Blessing - Lolita 138 kV, Lon Hill to Pawnee Switching Station 345 kV, Formosa - Lolita 138 kV, Coleto Creek - Victoria 138 kV | RT | Forced
AEP | Airline Aep - … - Westside Aep | LN | 138 | 18/1 | Barney Davis to Nelson Sharpe 138 kV, Nelson Sharpe Auto Trx Xf1 345/138 kV | Rodd Field - Holly 138 kV | RT | Planned
AEP | Airline Aep - Holly | LN | 138 | 18/1 | Barney Davis to Nelson Sharpe 138 kV, Nelson Sharpe Auto Trx Xf1 345/138 kV | Rodd Field - Holly 138 kV | RT | Planned
AEP | Ajo - Rio Hondo | LN | 345 | 16/2, 17/2 | DCKT Lon Hill to North Edinburg 345 kV & Orange Grove Sw 138 kV | Celanese Bishop - Nelson Sharpe 138 kV, Lon Hill - Bessel 138 kV | ST | Planned
AEP | Alpine - … - Barrilla | LN | 69 | 17/9 | Fort Stockton Plant to Re Roserock Solar Plant & Solstice 138 kV | Barilla - Fort Stockton Sw 69 kV | RT | Planned
AEP | Armstrong Aep - … - Raymondville 2 | LN | 138 | 16/3 | Valley Import | N/A | RT | Forced
AEP | Aspermont Aep - Paint Creek | LN | 138 | 16/4 | Scurry Sw to Sun Sw 138 kV | Paint Creek Auto 69-2 138/69 kV | RT | Forced
AEP | Barney Davis Bus #1 (CB 6755, etc.) | BUS | 138 | 16/10 | DCKT Barney Davis to Airline Aep 138 kV | Barney Davis - Rodd Field 138 kV | ST | Planned | Y
AEP | Barney Davis Bus #2 (CB 5200, etc.) | BUS | 138 | 16/10, 17/2, 17/3 | Airline Aep to Barney Davis 138 kV | Rodd Field - Holly 138 kV | ST | Planned, Forced | Y
AEP | Barrilla - Fort Stockton Sw | LN | 69 | 18/4 | Fort Stockton Plant to Re Roserock Solar Plant & Solstice 138 kV | Yucca Drive Sw - Gas Pad 138 kV | RT | Planned
AEP | Bates - … - North Edinburg & Palmhurst | LN | 138 | 17/11 | DCKT Haisley to Warburton Road Switching Station 138 kV & Lon Hill to Coleto Creek 345 kV | Lon Hill - Pawnee Switching Station 345 kV | RT | Planned
AEP | Beeville - … - Victoria | LN | 69 | 17/4 | Hecker to WhitePoint 138 kV | Whitepoint - Rincon 138 kV | RT | Planned
AEP | Bevo - Asherton | LN | 138 | 15/11 | Basecase | Low Voltage from Dimmit to DC Eagle Pass | ST | Forced
AEP | Big Three - … - Bp Chem Vistron4 | LN | 138 | 17/6 | DCKT Victoria to Victoria Dupont Sw & Victoria Dupont Sw to Victoria 138 kV | Formosa - Lolita 138 kV | RT | Planned, Forced
AEP | Blessing - Stp Sw | LN | 138 | 18/1 | Lane City to Blessing 138 kV | El_Campo - Lane City Pump 138 kV | RT | Forced
AEP | Blessing Auto 1382 138/69 kV | XF | 138 | 17/10, 17/12 | Coleto Creek to Victoria 138 kV, DCKT San Miguel Gen to Elmcreek 345 kV, San Miguel Auto 345_138 kV Switchyards Trx SANMGL8_3_1 | Coleto Creek - Victoria 138 kV, Pawnee Switching Station - Calaveras 345 kV, San Miguel Auto ATAH 345/138 KV | RT | Planned
AEP | Bruni - Crestonio | LN | 138 | 15/5, 15/6 | Laquinta to Lobo 138 kV | Bruni Auto 69_1 138/69 kV | ST | Planned | Y, N
AEP | Celanese Bishop Bus #1 (CB 6305, 8425) | BUS | 138 | 16/10 | Airline Aep to Barney Davis 138 kV | Rodd Field - Holly 138 kV | ST | Planned | Y
AEP | Celanese Bishop Bus #2 (CB 6075, 8425) | BUS | 138 | 16/10 | Airline Aep to Barney Davis 138 kV | Rodd Field - Holly 138 kV | ST | Planned | Y
AEP | Coleto - Lon Hill | LN | 345 | 17/3, 15/3, 16/1, 16/12 | DCKT Whitepoint to Hecker & Dupont Sw Ingleside 138 kV, Coleto Creek to Pawnee Sw 345 kV, Pawnee Sw to Lon Hill 345 kV | Whitepoint - Rincon 138 kV, Kenedy Sw - Coleto Creek 138 kV, Magruder - Victoria 138 kV, Kenedy Sub - Kenedy Sw 69 kV | RT, ST | Planned, Forced | Y, N
AEP | Coleto - Victoria (COLETO_VICTOR1) | LN | 138 | 17/4 | Coleto Creek 345_138h 345/138 kV | Coleto Creek - Victoria 138 kV | RT | Planned
AEP | Del Sol - … - North Edinburg | LN | 345 | 16/10, 17/1 | Valley GTC | N/A | ST | Planned | Y
AEP | Dupont Sw Ingleside - ... - Portland | LN | 138 | 15/1 | DCKT Dupont Sw Ingleside to Whitepoint & Hecker 138 kV | Rincon - Whitepoint 138 kV | ST | Planned
AEP | Eagle Hydro Tap - … - Hamilton Road | LN | 138 | 18/3 | North McCamey to Santa Rita 138 kV | Santiago - San Angelo Power Station 138 kV | RT | Planned
AEP | Fannin Sub - Victoria | LN | 69 | 17/4 | Coleto Creek 345_138h 345/138 kV | Coleto Creek - Victoria 138 kV | RT | Planned
AEP | Fort Stockton Plant - … - Fort Stockton Sw | LN | 69 | 18/3, 18/4 | Fort Stockton Plant to Oxy Century Tnp & Rio Pecos & Woodward 1 138 kV, Fort Stockton Plant to Re Roserock Solar Plant & Solstice 138 kV | Yucca Drive Sw - Gas Pad 138 kV, 16Th Street Tnp - Woodward 2 138 kV, Barilla - Fort Stockton Sw 69 kV, Pig Creek - Solstice 138 kV | RT | Planned
AEP | Fort Stockton Plant - Conoco Comp Station | LN | 69 | 18/3, 18/4 | Fort Stockton Plant to Re Roserock Solar Plant & Solstice 138 kV | Barilla - Fort Stockton Sw 69 kV, Yucca Drive Sw - Gas Pad 138 kV | RT | Planned
AEP | Fort Stockton Plant - Solstice | LN | 138 | 17/12 | Basecase, Barrilla Auto Trx Fmr1 138/69 kV | Yucca Drive Sw - Gas Pad 138 kV | RT | Planned
AEP | Fort Stockton Plant Auto 69T1 138/69 kV | XF | 138 | 17/12, 18/3, 18/4 | Basecase, Barrilla Auto Trx Fmr1 138/69 Kv, Barilla to Solstice 138 kV, Fort Stockton Plant to Oxy Century Tnp & Rio Pecos & Woodward 1 138 kV | Yucca Drive Sw - Gas Pad 138 Kv, Alamito Creek - Paisano 69 kV, 16Th Street Tnp - Woodward 2 138 kV, Pig Creek - Solstice 138 kV | RT | Planned
AEP | Fort Stockton Sw - … - Rio Pecos | LN | 69 | 17/12, 18/1 | Fort Stockton Plant to Re Roserock Solar Plant & Solstice 138 kV, Barilla to Solstice 138 kV | Barilla - Fort Stockton Sw 69 kV, Alamito Creek - Paisano 69 kV | RT | Forced
AEP | Frontera - … - Key Sw & Palmhurst | LN | 138 | 17/5 | Pharr Magic Valley to North Pharr 138 kV | North McAllen - West McAllen 138 KV | RT | Planned
AEP | Frontera - Bates | LN | 138 | 17/8 | DCKT San Miguel Gen to Elmcreek 345 kV | Pawnee Switching Station - Calaveras 345 kV | RT | Planned
AEP | Fulton - … - Rockport | LN | 69 | 17/9, 17/11 | DCKT San Miguel Gen to Elmcreek 345 kV, DCKT Haisley to Warburton Road Switching Station 138 kV & Lon Hill to Coleto Creek 345 kV | Lon Hill - Pawnee Switching Station 345 kV, Pawnee Switching Station - Calaveras 345 kV | RT | Forced
AEP | Gateway - … - North Laredo Sw & Wormser Road | LN | 138 | 18/4 | Kendall to Cagnon 345 kV | CICO - Comfort 138 kV | RT | Forced
AEP | Gila - … - Whitepoint | LN | 138 | 17/8 | DCKT San Miguel Gen to Elmcreek 345 kV | Pawnee Switching Station - Calaveras 345 kV | RT | Forced
AEP | Haine Drive - La Palma | LN | 138 | 17/4 | DCKT Rio Hondo to North Endinburg 345 kV & Harlingen Sw | Burns Sub - Rio Hondo 138 kV | RT | Planned
AEP | Hamilton Road - Brackettville | LN | 138 | 18/4 | DCKT Big Hill to Kendall 345 kV | Hamilton Road - Maverick 138 kV | RT | Planned
AEP | Harlingen #1 - … - La Palma | LN | 69 | 18/1 | Lon Hill to Coleto Creek 345 kV, Dyann to Wharton 138 kV, La Palma to East Harrison 69 kV, North Edinburg Auto Trx 1382 345/138 kV | Warburton Road Switching Station - Victoria 138 kV, El_Campo - Lane City Pump 138 kV, North Edinburg Auto 138H 345/138 kV | RT | Forced
AEP | Hecker - Dupont Sw Ingleside (HECKER_I_DUPS0) | LN | 138 | 17/4 | Hecker to WhitePoint 138 kV | Whitepoint - Rincon 138 kV | RT | Planned
AEP | Hecker - Dupont Sw Ingleside (HECKER_I_DUPS2) | LN | 138 | 17/4 | Hecker to WhitePoint 138 kV | Whitepoint - Rincon 138 kV | RT | Planned
AEP | Hecker - Whitepoint (HECKER_WHITE_1) | LN | 138 | 17/3, 18/1 | DCKT Whitepoint to Hecker & Dupont Sw Ingleside 138 kV, Lon Hill to Coleto Creek 345 kV | Whitepoint - Rincon 138 kV, Warburton Road Switching Station - Victoria 138 kV | RT | Planned, Forced
AEP | Hecker - Whitepoint (HECKER_WHITE_2) | LN | 138 | 18/1 | Lon Hill to Coleto Creek 345 kV | Warburton Road Switching Station - Victoria 138 kV | RT | Forced
AEP | Hiway 9 Auto 69A2 138/69 kV | XF | 138 | 17/4 | Lon Hill Auto 69A1 138/69 kV | Koch Up River Auto 69A1 138/69 kV | RT | Forced
AEP | Industrial Aep - Nueces Bay | LN | 69 | 17/4 | Lon Hill Auto 69A1 138/69 kV | Koch Up River Auto 69A1 138/69 kV | RT | Forced
AEP | Ingleside - Aransas Pass | LN | 138 | 17/8 | Lon Hill to Coleto Creek 345 Kv | Lon Hill - Pawnee Switching Station 345 kV | RT | Forced
AEP | Ingleside - Dupont Sw | LN | 138 | 17/4 | Rockport to Rincon 138 kV | Gregory - Rincon 69 kV | ST | Forced
AEP | Jim Treece - Riley | LN | 345 | 16/11 | Panhandle GTC | N/A | ST | Planned
AEP | Jim Treece - Tesla | LN | 345 | 16/11 | Panhandle GTC | N/A | ST | Planned | Y
AEP | Joslin Bus #1 (CB 8315, etc.) | BUS | 138 | 17/3 | Formosa Unit FORMOSG12, Formosa Unit FORMOSG3 | Formosa - Lolita 138 kV | RT | Planned
AEP | La Palma - … - Stewart Road | LN | 69 | 18/1 | North Edinburg Auto Trx 1382 345/138 kV | North Edinburg Auto 138H 345/138 kV | RT | Forced
AEP | La Palma Bus #2 (CB 5875, etc.) | BUS | 138 | 17/2 | North Edinburg Auto 1382 345/138 kV | Burns Sub - Rio Hondo 138 kV | RT | Planned
AEP | Laredo Vft North - … - Mines Road | LN | 138 | 18/4 | Molina to Wormser Road 138 kV, Lobo to Molina 138 kV | Del_Mar - Laredo Plant 138 kV | RT | Planned
AEP | Las Pulgas - Raymondville 2 | LN | 138 | 17/4 | DCKT Rio Hondo to North Endinburg 345 kV & Harlingen Sw | Burns Sub - Rio Hondo 138 kV | RT | Planned
AEP | Las Pulgas - Rio Hondo | LN | 138 | 17/4 | Loyola Sub to Kleberg Aep 138 kV | Loyola Sub Auto 69_1 138/69 kV | ST | Planned
AEP | Liston - Garza | LN | 138 | 18/4 | DCKT Big Hill to Kendall 345 kV | Hamilton Road - Maverick 138 kV | RT | Planned
AEP | Lobo - Laquinta | LN | 138 | 15/5 | Crestonio to Falfurrias 138 kV | Bruni Auto 69_1 138/69 kV | ST | Planned | Y
AEP | Lobo - Laredo Vft North | LN | 138 | 15/4 | Laredo VFT North to Lobo 138 kV | Asherton - Catarina 138 kV | ST | Planned
AEP | Lobo Auto A1 345/138 kV | XF | 345 | 17/6 | Lobo Auto Trx A2 345/138 kV | Asherton - Catarina 138 kV | RT | Forced
AEP | Lolita - Victoria | LN | 138 | 17/5 | DCKT Victoria to Victoria Dupont Sw & Victoria Dupont Sw to Victoria 138 kV | Blessing - Lolita 138 kV, Formosa - Lolita 138 kV | RT | Planned
AEP | Lon Hill - Nelson Sharpe | LN | 345 | 15/2, 15/10, 16/3, 16/4 | DCKT Lon Hill to North Edinburg 345 kV & Orange Grove Sw 138 kV, Ajo to Rio Hondo 345 kV | Bunsen - Lon Hill 138 kV, Celanese Bishop - Kleberg 138 kV | ST | Planned | Y
AEP | Lon Hill - Whitepoint | LN | 345 | 17/8, 18/2 | Lon Hill to Coleto Creek 345 kV, DCKT San Miguel Gen to Elmcreek 345 kV, DCKT Kendall to Cagnon 345 kV & Menger Creek to Ranchtwn 138 kV | Lon Hill - Pawnee Switching Station 345 kV, Pawnee Switching Station - Calaveras 345 kV, Marion Auto AT2H 345/138 kV | RT | Forced
AEP | Lon Hill Auto 69A2 138/69 kV | XF | 138 | 17/4 | Hecker to WhitePoint 138 kV, Lon Hill Auto 69A1 138/69 kV | Whitepoint - Rincon 138 kV, Koch Up River Auto 69A1 138/69 kV | RT | Planned
AEP | Lon Hill Bus #1 (CB 6005, etc.) | BUS | 138 | 15/5 | Lobo Auto A2 345/138 kV | Asherton - Catarina 138 kV | ST | Planned
AEP | Mvec (Rangerville) - … - Wesmer | LN | 138 | 18/2 | Polk Avenue to North Pharr 138 kV | North McAllen - West McAllen 138 KV | RT | Planned
AEP | Naval Base - … - Port Aransas | LN | 69 | 17/4 | Hecker to WhitePoint 138 kV | Whitepoint - Rincon 138 kV | RT | Planned
AEP | North Edinburg - Lon Hill | LN | 345 | 17/3, 15/3, 16/3 | Nelson Sharpe to Ajo 345 kV, Nelso Sharpe to Ajo 345 kV, DCKT Rio Hondo to North Edinburg 345 kV & Harlingen Sw 138 kV, Valley GTC | Raymondville 2 - Yturria Sub 138 kV, Celanese Bishop - Nelson Sharpe 138 kV, Burns Sub - Rio Hondo 138 kV, N/A | RT, ST | Planned, Forced
AEP | North Edinburg - Rio Hondo | LN | 345 | 16/3 | North Edinburg to Lon Hill 345 kV | Burns Sub - Rio Hondo 138 kV | ST | Planned
AEP | North Edinburg Auto 138 345/138 kV | XF | 345 | 17/2 | North Edinburg Auto 1382 345/138 kV | Burns Sub - Rio Hondo 138 kV | RT | Planned
AEP | North Edinburg Bus #1 (CB 5010, etc.) | BUS | 138 | 16/9 | North McAllen to North Edinburg 138 kV | North Edinburg - McColl Road 138 kV | ST | Planned
AEP | North McAllen - North Pharr | LN | 138 | 17/5 | Pharr Magic Valley to North Pharr 138 kV | North McAllen - West McAllen 138 KV | RT | Planned
AEP | Paint Creek Bus #1 (CB 4135, etc.) | BUS | 138 | 16/5, 16/6, 17/1 | Scurry Sw to Sun Sw 138 kV, Salt Creek Bepc to Salt Creek Reactor 138 kV | Eskota Sw - Longworth 69 kV, Aspermont Auto 69T1 138/69 kV | ST | Planned
AEP | Pig Creek - Musquiz | LN | 138 | 17/9 | Yucca Drive Sw to Wolf Switching Station 138 kV | Andrews County South - Amoco Three Bar Tap 138 kV, No Trees Sw - Cheyenne Tap 138 kV | RT | Planned
AEP | Pig Creek - Solstice | LN | 138 | 17/9 | Fort Stockton Plant to Re Roserock Solar Plant & Solstice 138 kV | Barilla - Fort Stockton Sw 69 kV | RT | Planned
AEP | Port Aransas - Seawall Aep | LN | 69 | 17/3, 18/1 | DCKT Whitepoint to McCambell & Dupons Sw Ingleside 138 kV, DCKT Whitepoint to Hecker & Dupont Sw Ingleside 138 Kv, Barney Davis to Nelson Sharpe 138 kV, Nelson Sharpe Auto Trx Xf1 345/138 kV | Whitepoint - Rincon 138 kV, Rodd Field - Holly 138 kV | RT | Planned, Forced
AEP | Raymondville 2 - … - Rio Hondo | LN | 138 | 16/12 | Loyola Sub to Kleberg Aep 138 kV | Loyola Sub Auto 69_1 138/69 kV | ST | Planned
AEP | Rio Hondo - La Palma | LN | 345 | 17/12 | Danevang Switching Station to Blessing 138 kV, DCKT San Miguel Gen to Elmcreek 345 kV, San Miguel Auto 345_138 kV Switchyards Trx SANMGL8_3_1 345/138 kV | Blessing Auto 69A1 138/69 kV, Pawnee Switching Station - Calaveras 345 kV | RT | Planned
AEP | Rockport Auto 69A1 138/69 kV | XF | 138 | 17/9 | Lon Hill to Coleto Creek 345 kV | Lon Hill - Pawnee Switching Station 345 kV | RT | Forced
AEP | Rockport Auto T2 138/69 kV | XF | 138 | 17/9 | Lon Hill to Coleto Creek 345 kV | Lon Hill - Pawnee Switching Station 345 kV | RT | Forced
AEP | San Angelo Concho - Rusthill | LN | 138 | 15/6 | San Angelo College Hills Auto 69T1 138/69 kV | San Angelo Power Station Auto 69T1 138/69 kV | RT | Forced
AEP | San Angelo Concho Auto 69T1 | XF | 138 | 15/2, 15/6, 15/7 | San Angelo North Auto 69T1 138/69 kV, San Angelo College Hills Auto 69T1 138/69 kV | San Angelo College Hills Auto 69T1 138/69 kV, San Angelo Power Station Auto 69T1 138/69 kV | RT | Planned, Forced
AEP | San Angelo Red Creek Auto T2 345/138 kV | XF | 345 | 16/10 | San Angelo Red Creek Auto T1 345/138 kV | Nicole - Orient 138 kV | RT | Planned
AEP | Solstice to Alamito Creek | LN | 138 | 18/2 | Fort Stockton Plant to Re Roserock Solar Plant & Solstice 138 kV | Barilla - Fort Stockton Sw 69 kV | RT | Forced
AEP | Sonora Auto 69-1 138/69 kV | XF | 138 | 18/3 | North McCamey to Santa Rita 138 kV | Santiago - San Angelo Power Station 138 kV | RT | Planned
AEP | South Carbide - Hwy 511 Sub | LN | 138 | 16/6 | South Carbide to Loma Alta Sub 138 kV | La Palma - Villa Cavazos 138 kV | ST | Planned
AEP | Tesla - Jim Treec | LN | 345 | 17/2 | Panhandle GTC | N/A | ST | Planned
AEP | West Batesville Bus #1 (CB 1005, etc.) | BUS | 138 | 15/4 | Lobo to San Miguel 345 kV | Hamilton Road - Maverick 138 kV | ST | Planned
AEP | Whitepoint Auto 345A 345/138 kV | XF | 345 | 18/3 | Lon Hill Auto Trx Lon_Hill_3_2 345/138 kV | Lon Hill Auto 381H 345/138 kV | RT | Forced
AEP | Whitepoint Bus #0010 (CB 3900, etc.) | BUS | 345 | 18/3 | DCKT Menger Creek to Cico 138 kV & Kendall to Cagnon 345 kV | Medina Lake - Tally Rd 138 kV | RT | Forced
AEP | Whitepoint Bus #0014 (CB 3930, etc.) | BUS | 345 | 18/3 | DCKT Menger Creek to Cico 138 kV & Kendall to Cagnon 345 kV | Medina Lake - Tally Rd 138 kV | RT | Forced
AEP, BRAZOS | Salt Creek Bepc - … - Spur | LN | 138 | 16/3, 16/10 | Aspermont Aep to Spur 138 kV | Spur Auto 69_1 138/69 kV | ST | Planned | Y, N
AEP, CNP | Whitepoint - South Texas Project | LN | 345 | 17/9, 17/11, 17/12, 18/1, 18/3 | Lon Hill to Coleto Creek 345 kV, DCKT San Miguel Gen to Elmcreek 345 kV, DCKT Haisley to Warburton Road Switching Station 138 kV & Lon Hill to Coleto Creek 345 kV, San Miguel Auto 345_138 kV Switchyards Trx SANMGL8_3_1 345/138 kV, Dyann to Wharton 138 kV, Danevang Switching Station to Blessing 138 kV | Lon Hill - Pawnee Switching Station 345 kV, Pawnee Switching Station - Calaveras 345 kV, Blessing Auto 69A1 138/69 kV, El_Campo - Lane City Pump 138 kV | RT | Forced
AEP, CROSS | Gray - Tesla (GRAY_TESLA_1) | LN | 345 | 17/1 | Panhandle GTC | N/A | RT | Forced
AEP, CROSS, SHARYLAND | Tesla - … - Tule Canyon (1) | LN | 345 | 16/5, 16/11, 16/12 | Panhandle GTC | N/A | RT, ST | Planned, Forced
AEP, CROSS, SHARYLAND | Tesla - … - Tule Canyon (2) | LN | 345 | 16/5, 16/11, 16/12 | Panhandle GTC | N/A | RT, ST | Planned, Forced
AEP, ETT | Clear Crossing - … - Edith Clarke (EDITHC_GAUSS2) | LN | 345 | 17/7, 17/8, 17/9 | Basecase | Panhandle GTC | RT | Planned
AEP, ETT | Edith Clarke - Riley (Edithc_Riley1) | LN | 345 | 17/10, 17/11, 17/12, 18/1, 18/2, 18/3 | Panhandle GTC | N/A | RT | Planned
AEP, ETT | Edith Clarke - Riley (Edithc_Riley2) | LN | 345 | 17/10, 17/11, 17/12, 18/1, 18/2, 18/3 | Panhandle GTC | N/A | RT | Planned
AEP, LCRA | Mesa View Sw - … - Tunas Creek | LN | 138 | 18/3 | North McCamey to Santa Rita 138 kV | Santiago - San Angelo Power Station 138 kV | RT | Planned
AEP, ONCOR | Clear Crossing - … - Dermott Sw (DMTSW_KIRCHH1) | LN | 345 | 18/4 | DCKT Dermott Sw to Scurry County South Sw 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned
AEP, ONCOR | Clear Crossing - … - Dermott Sw (DMTSW_KIRCHH2) | LN | 345 | 18/4 | DCKT Dermott Sw to Scurry County South Sw 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned
AEP, ONCOR | Permian Basin Ses - … - Yucca Drive Sw (6427, 6332_A) | LN | 138 | 18/3, 18/4 | Fort Stockton Plant to Oxy Century Tnp & Rio Pecos & Woodward 1 138 kV, Fort Stockton Plant to Re Roserock Solar Plant & Solstice 138 kV | 16Th Street Tnp - Woodward 2 138 kV, Yucca Drive Sw - Gas Pad 138 kV | RT | Planned, Forced
AEP, SHARYLAND | Frontera - … - Railroad | LN | 138 | 18/3 | Polk Avenue to North Pharr 138 kV | North McAllen - West McAllen 138 KV | RT | Planned
AEP, SHARYLAND | North Edinburg - Palmito | LN | 345 | 18/1 | Basecase | Valley Import | RT | Forced
AEP, STEC | Calallen Sub - … - Stadium Aep | LN | 69 | 18/3 | Lon Hill Auto 382H 345/138 kV | Lon Hill Auto 381H 345/138 kV | RT | Planned
AEP, STEC | Danevang Switching Station - Blessing | LN | 138 | 17/5 | DCKT Victoria to Victoria Dupont Sw & Victoria Dupont Sw to Victoria 138 kV | Formosa - Lolita 138 kV | RT | Planned
AEP, STEC | George West Switching Station - … - Orange Grove Switching Station | LN | 138 | 18/1 | San Miguel Auto 345_138 kV Switchyards Trx Sanmgl8_3_2 345/138 kV | San Miguel Gen Auto ATBH 345/138 kV | RT | Forced
AEP, STEC | La Sara Sub - … - Raymondville 2 | LN | 138 | 18/4 | San Miguel Gen to Elmcreek 345 kV | Pawnee Switching Station - Calaveras 345 kV | RT | Forced |  | Doug Evans | The Contingency and Overload look completely realistic, but La Sara to Raymondville tap is not significant enough to be an MTE. La Sara to Raymondville Tap is a radial 138 kV line in the LRG Valley that connects to AEP's Raymondville #2. Raymondville Tap to Raymondville #2 is also radial. The projected summer peak load at La Sara for 2018 is less than 8 MW. If ERCOT's system showed a shift factor for the outage of this line having an effect on the Calaveras to Pawnee line then ERCOT's system did not reach a correct solution or the wrong MTE was put in this row. If La Sara to Raymondville 2 causes an impact to Calaveras to Pawnee then every non-radial line south of Corpus Christi needs to be on this list. Please remove this or check your data and bring proof that this line needs to be on the list. The only explanation is that the La Sara to Raymondville just happened to be out when the Contingency and Overload occurred.
AEP, STEC | Lobo - San Miguel | LN | 345 | 15/11, 16/4 | Rio Bravo to Zapata 138 kV, Javalina Tap to Rio Bravo 138 kV | Freer - San Diego 69 kV, Voltage Collapse | ST | Planned |  | Doug Evans | STEC and AEP have been working for several years to close the normally open tie at San Diego between AEP and STEC. All of the relay additions and coordination has been completed. The only thing remaining is for AEP to implement the relay settings and test their relays. STEC suspects that this voltage collapse, assuming it is in the Freer-San Diego area, would be mitigated enough for this to be taken off the list once AEP has completed the work. AEP is there an expected date for the relay work to be completed? If the voltage collapse is closer to Laredo this could be valid.
AEP, STEC | Loop 463 - Victoria | LN | 138 | 16/3 | Four Corners to Sam Rayburn Sw 138 kV | Sam Rayburn Switching Station Auto 69_2 138/69 kV | ST | Planned |  | Doug Evans | See Loop 463 - Victoria tab
AEP, STEC | Moore Sw - Downie Sw | LN | 138 | 16/10, 17/4 | Downie Switching Station to Uvalde Aep 138 kV | Downie Switching Station Auto AX1 138/69 kV | ST | Planned | Y | Doug Evans | A TOAP could be created for outage of either of the two 138 kV lines from Downie. The 95 MW Helios Solar plant is the only generation connected to Downie. If both 138 kV lines are out then all of Helios output goes through the Downie 138/69 kV 50 MVA auto. As long as the solar plant can back down below 50 MVA within a set time (TBD) we can avoid backing their generation preemptively. Another option would be to set up a SCADA control opening of the breaker to trip Helios off if both 138 kV lines are open. Then STEC TSP operator can work with the QSE to bring 50 or less MW back online.
AEP, STEC | Orange Grove Switching Station - Lon Hill | LN | 138 | 18/1 | San Miguel Auto 345_138 kV Switchyards Trx Sanmgl8_3_2 345/138 kV | San Miguel Gen Auto ATBH 345/138 kV | RT | Forced
AEP, WET | Edith Clarke - Wett_Cottonwood (COTTON_EDITHC3) | LN | 345 | 16/11, 16/12, 17/1, 17/2, 17/3, 17/4, 17/5, 17/6 | Panhandle GTC | N/A | RT, ST | Planned, Forced
AEP, WET | Edith Clarke - Wett_Cottonwood (COTTON_EDITHC4) | LN | 345 | 16/11, 16/12, 17/1, 17/2, 17/3, 17/4, 17/5, 17/6 | Panhandle GTC | N/A | RT, ST | Planned, Forced
BPUB | Loma Alta Substation - Waterport Substation | LN | 138 | 18/1 | La Palma to East Harrison 69 kV | Haine Drive - La Palma 138 kV | RT | Forced
BPUB | Palo Alto Sub - Titan Sub | LN | 138 | 16/5 | South Carbide to Loma Alta Sub 138 kV, Loma Alta Sub T1 138/69 kV | La Palma - Villa Cavazos 138 kV | RT | Planned
BPUB | Power Plant Substation - Sixth Street Substation | LN | 138 | 18/3, 18/4 | DCKT San Miguel Gen to Elmcreek 345 kV, Kendall to Cagnon 345 kV | Pawnee Switching Station - Calaveras 345 kV, CICO - Comfort 138 kV | RT | Planned
BPUB | South Plant Substation - Sixth Street Substation | LN | 138 | 18/3, 18/4 | DCKT San Miguel Gen to Elmcreek 345 kV, Kendall to Cagnon 345 kV; | Pawnee Switching Station - Calaveras 345 kV, CICO - Comfort 138 kV | RT | Planned
BPUB | Waterport Sub - Loma Alta Sub 138 kV | LN | 138 | 16/5 | South Carbide to Loma Alta Sub 138 kV, Loma Alta Sub T1 138/69 kV | La Palma - Villa Cavazos 138 kV | RT | Planned
BPUB | Waterport Sub - Southmost Sub | LN | 138 | 18/1 | Lon Hill to Coleto Creek 345 kV, La Palma to East Harrison 69 kV, DCKT Jewett to Singleton 345 kV | Warburton Road Switching Station - Victoria 138 kV, Btu Jack Creek - Twin Oak Sw 345 kV | RT | Forced
BPUB, TMPA | Gibbons Creek - Btu_Jack_Creek | LN | 345 | 17/4, 16/1 | DCKT Jewett to Singleton 345 kV | Gibbons Creek - Twin Oak Sw 345 kV, BTU_Jack_Creek Auto XF1 345/138 kV | RT, ST | Planned | Y
BRAZOS | Hasse Auto Xfm1 138/69 kV | XF | 138 | 17/11 | Brownwood Sw to Mercers Gap Sw 138 kV, Comanche Sw (Oncor) to Mercers Gap Sw | Has Auto XFM2 138/69 kV | RT | Forced
BRAZOS | Hilltop Lakes - Watson Chapel | LN | 138 | 17/8 | DCKT Jewett to Singleton 345 kV | Btu Jack Creek - Twin Oak Sw 345 kV | RT | Planned
BRAZOS | Jaybird - Stephenville Bepc | LN | 138 | 16/11 | Mineral Wells to Mineral Wells West 138 kV | Bunker - RW Miller 138 kV | ST | Planned
BRAZOS | Lewisville Sw Auto FMR2 345/138 kV | XF | 345 | 17/4 | Jones Street Tnp to Lewisville Sw 138 kV | Ti Tnp - West Tnp 138 kV | RT | Planned
BRAZOS | Navo - Krugerville | LN | 138 | 15/10 | Jim Christal Sub to West Denton 138 kV | Pockrus Sub - Teasely Sub 138 kV | ST | Forced
BRAZOS | Rw Miller - Jaybird | LN | 138 | 16/11 | Mineral Wells to Mineral Wells West 138 kV | Bunker - RW Miller 138 kV | ST | Planned
BRAZOS | Stephenville Bepc Auto FMR1 | XF | 138 | 15/3 | Oran Sub to Mineral Wells & RW Miller 138 kV | Bunker - RW Miller 138 kV | ST | Planned
BRAZOS | Whitney Bus 1525 (CB 5075, etc.) | BUS | 138 | 16/12 | Bosque Sw to Elm Mott 345 kV | Bosque Sw - Rogers Hill Bepc 138 kV | ST | Forced
BRAZOS | Whitney Bus BB1 (CB 210, etc.) | BUS | 69 | 16/12 | Bosque Sw to Elm Mott 345 kV | Bosque Sw - Rogers Hill Bepc 138 kV | ST | Forced
BRAZOS, DME, ONCOR | Arco - Navo - Collin Ses | LN | 138 | 16/6, 16/7, 16/8, 16/9, 17/3 | Fort Worth Sub to West Denton 138 kV, Jim Christal Sub to West Denton 138 kV, DCKT Lewisville Sw to Krum West Sw & Roanoke Sw 345 kV | Jim Christal Sub - West Denton 138 kV, Fort Worth Sub - West Denton 138 kV, Corinth (Oncor) - Pockrus Sub 138 kV | RT | Planned
BRAZOS, ONCOR | Carrollton Northwest - Lewisville Sw | LN | 345 | 17/3 | Jones Street Tnp to Lewisville | Ti Tnp - West Tnp 138 kV | RT | Planned
BRAZOS, ONCOR | Keller - … - Roanoke Sw | LN | 138 | 17/11 | DCKT Eagle Mountain to Saginaw Sw 138 Kv | Eagle Mountain Ses - Eagle Mountain Compressor 138 kV | RT | Planned
BRAZOS, ONCOR | Navarro - … - Trinidad Ses | LN | 138 | 17/12 | DCKT Desoto Sw to Cedar Hill Sw & Cedar Hill Sw to Watermill Sw 345 kV | Seagoville - Kleberg Tap | RT | Planned
BRAZOS, ONCOR | Plano Communication Parkway - Spring Creek | LN | 138 | 17/10 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 Kv | Wagley Robertson - Summerfield 138 kV | RT | Planned
BRAZOS, ONCOR | Rhome Bepc - … - Roanoke Sw (RNKSW_ELZBTHCK) | LN | 138 | 17/10 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Wagley Robertson - Summerfield 138 KV | RT | Planned
BRAZOS, TMPA | Gibbons Creek - Keith Sw 138 kV | LN | 138 | 16/10 | Gibbons Creek to Btu_East 138 kV | Gibbons Creek - Btu_Greens_Prairie 138 kV | RT | Planned
BTU | Btu_Dansby - Btu_Atkins | LN | 138 | 17/3 | Btu_Industrial_Park to Btu_North 69 kV | Btu_East - Btu_Shady_Lane 69 kV | RT | Planned
BTU | Btu_Dowling - Btu_Enterprise | LN | 138 | 18/3 | DCKT Jewett to Singleton 345 kV | Btu Jack Creek - Twin Oak Sw 345 kV | RT | Forced
BTU | Btu_Dowling - Btu_Texas_Am | LN | 138 | 17/3 | Btu_Industrial_Park to Btu_North 69 kV | Btu_East - Btu_Shady_Lane 69 kV | RT | Planned
BTU | Btu_East - Btu_Shady_Lane 69 | LN | 69 | 16/6 | Btu_Atkins Auto FMR1 138/69 kV | Btu_Briarcrest - Btu_Nall_Lane 69 kV | RT | Forced
CNP | Airpro - Quanum | LN | 138 | 17/5 | DCKT Chambers to King & Cedar Bayou Plant to Jordan 345 kV | Channelview - Lynch 138 kV | RT | Planned
CNP | Airpro - Shell | LN | 138 | 16/8, 18/1 | DCKT Chambers to King & Cedar Bayou to Jordan 345 kV, Ph Robinson to Center 345 kV | Aritek - Chorin 138 kV, Cedar Bayou Plant - Strang 138 kV | RT | Planned, Forced
CNP | Arcola - … - Wa Parish (TM_WAP82) | LN | 138 | 17/10 | DCKT Jewett to Singleton 345 kV | Btu Jack Creek - Twin Oak Sw 345 kV | RT | Planned
CNP | Bellaire - … - Britmoore (BI_UL_24) | LN | 138 | 17/11 | Comanche Sw (Oncor) to Mercers Gap Sw | Has Auto XFM2 138/69 kV | RT | Planned
CNP | Bellaire - … - Jeanetta | LN | 138 | 17/10 | DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 kV | Singleton - Zenith 345 kV | RT | Planned
CNP | Bellaire - Wa Parish | LN | 345 | 16/10 | DCKT Wa Parish to Jeanetta 345 kV | Bellaire - Smithers 345 kV | ST | Planned
CNP | Bigvue - Power Systems Arco Cogen | LN | 138 | 17/4 | DCKT Cedar Bayou Plant to Quanum & Strang 138 kV | Channelview - Lynch 138 kV | RT | Planned
CNP | Biport - … - Riwood | LN | 138 | 17/6 | DCKT Dow Chemical to Oasis 345 kV | Sintek to Stratt 138 kV | RT | Planned
CNP | Bunker - … - Stadium | LN | 138 | 18/4 | DCKT Jewett to Singleton 345 kV | Btu Jack Creek - Twin Oak Sw 345 kV | RT | Planned
CNP | Cedar Bayou Plant - Strang | LN | 138 | 17/10 | Ph Robinson to Center 345 kV | Channelview - Lynch 138 kV, Exxon - Lynch 138 kV | RT | Planned
CNP | Center - Ph Robinson | LN | 345 | 16/5, 15/3, 16/3 | Meadow to Ph Robinson 345 kV, Ph Robinson Auto AT4 345/138 kV, DCKT Chambers to King & Cedar Bayou Plant to Jordan 345 kV, DCKT Cedar Bayou Plant to Chambers & Jordan 345 kV, DCKT Chambers to King & Cedar Bayou Plant to Jordan 345 kV | Meadow Auto AT1 345/138 kV, Cedar Bayou Plant Auto AT3 345/138 kV, Brine - Langston 138 kV, Cedar Bayou Plant - Strang 138 kV, Chorin - Strang 138 kV | RT, ST | Planned
CNP | Chorin - Aritek | LN | 138 | 17/5 | DCKT Chambers to King & Cedar Bayou Plant to Jordan 345 kV | Channelview - Lynch 138 kV | RT | Planned
CNP | Copper - … - Seaway & Velasco | LN | 138 | 18/1 | DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 kV | Singleton - Zenith 345 kV | RT | Planned
CNP | Fairbanks To - Th Wharton | LN | 138 | 17/11 | DCKT Jewett to Singleton 345 kV | Btu Jack Creek - Twin Oak Sw 345 kV | RT | Planned
CNP | Fairmont - … - Garden Villas (DR_GV_94) | LN | 138 | 18/1 | DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 kV | Singleton - Zenith 345 kV | RT | Planned
CNP | Garrott - Kirby (GT_KB_37) | LN | 138 | 17/9 | Meadow to Oasis 345 kV | Angleton - Liverpool 138 kV | RT | Planned
CNP | Goodyear - Lydell | LN | 138 | 17/4 | DCKT Greens Bayou to Gable & Hardy to Crockett 138 kV | Midtown - Garrott 138 kV | RT | Planned
CNP | Greens Bayou - … - Humble (GBYPW_94) | LN | 138 | 17/11 | DCKT Jewett to Singleton 345 kV | Gibbons Creek - Singleton 345 kV | RT | Planned
CNP | Greens Bayou Auto AT2 | XF | 345 | 16/2 | DCKT Greens Bayou to King 345 kV | Greens Bayou Auto AT1 345/138 kV | ST | Planned
CNP | Greens Bayou Bus #138A (CB G480, etc.) | BUS | 138 | 17/9 | Addicks to Th Wharton 345 Kv | Lauder - North Belt 138 kV | RT | Forced
CNP | Greens Bayou Bus #138B (CB G500, etc.) | BUS | 138 | 17/9 | Addicks to Th Wharton 345 Kv | Lauder - North Belt 138 kV | RT | Forced
CNP | Greens Bayou Bus #345A (CB A980, etc.) | BUS | 345 | 17/8, 17/9 | DCKT Mining to Deepwater & South Channel & Deepwater to Sr Bertron 69 kV, Addicks to Th Wharton 345 kV | Genral - University 69 kV, Lauder - North Belt 138 kV | RT | Forced
CNP | Greens Bayou Bus #345D (CB A990, etc.) | BUS | 345 | 17/8, 17/9 | DCKT Mining to Deepwater & South Channel & Deepwater to Sr Bertron 69 kV, Addicks to Th Wharton 345 kV | Genral - University 69 kV, Lauder - North Belt 138 kV | RT | Forced
CNP | H O Clarke - … - Southwyck | LN | 138 | 18/3 | DCKT Crown to Tanker & Davson to Greens Bayou 138 KV | Bigvue - Power Systems - Arco Cogen 138 kV | RT | Planned
CNP | Hillje - Wa Parish (HLJWAP64) | LN | 345 | 16/3 | DCKT South Texas Project to Dow Chemial & Jones Creek 345 kV | South Texas Project - Wa Parish 345 kV | RT | Planned
CNP | Jewett - Limestone (225) | LN | 345 | 15/3 | DCKT Limestone to Twin Oak Sw 345 kV | Big Brown Ses - Jewet (50) | ST | Planned
CNP | Jewett - Limestone (226) | LN | 345 | 15/3 | DCKT Limestone to Twin Oak Sw 345 kV | Big Brown Ses - Jewet (50) | ST | Planned
CNP | Jones Creek - Cortez | LN | 138 | 17/9 | DCKT Jewett to Singleton 345 kV | Gibbons Creek - Singleton 345 kV | RT | Planned
CNP | Jordan - North Belt | LN | 345 | 17/9, 17/10 | Meadow to Oasis 345 kV, Ph Robinson to Center 345 kV | Angleton - Liverpool 138 kV, Channelview - Lynch 138 kV, Exxon - Lynch 138 kV | RT | Forced
CNP | Marine - Cortez | LN | 138 | 17/11, 18/1 | DCKT Jewett to Singleton 345 kV | Btu Jack Creek - Twin Oak Sw 345 kV | RT | Planned, Forced
CNP | Moody - … - Stewart | LN | 138 | 18/1 | Ph Robinson to Center 345 kV | Cedar Bayou Plant - Strang 138 kV | RT | Forced
CNP | North Belt - … - Scenic Woods | LN | 138 | 17/10 | DCKT Jewett to Singleton 345 kV | Btu Jack Creek - Twin Oak Sw 345 kV; | RT | Planned
CNP | Oasis - Dow Chemical (DOWOAS27) | LN | 345 | 16/9 | DCKT WA Parish to Bailey & Hillje 345 kV | Oasis - Dow Chemical 345 kV (18) | RT | Planned, Forced
CNP | Petson - Monsan | LN | 138 | 17/10 | Petson to Monsan 138 kV | Intermediate - Southwyck 138 kV; | RT | Planned
CNP | Richmond Tank Switchrack - Chamon Power | LN | 138 | 17/11 | DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 Kv | Singleton - Zenith 345 kV | RT | Planned
CNP | Roans Prairie - Singleton | LN | 345 | 16/1 | DCKT Gibbons Creek to Singleton 345 kV | Jewett - Singleton 345 kV (240) | RT | Planned
CNP | Singleton - Zenith (SNGZEN98) | LN | 345 | 15/12, 17/1, 17/2, 17/3, 17/4, 15/7, 17/5, 17/10, 17/11 | DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 kV, DCKT Singleton to Tomball & Roans Prairie 345 kV, DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 kV, Kuykendahl to Rothwood 345 kV, DCKT Singleton to Tomball & Roans Prairie 345 kV | Singleton - Zenith 345 kV (99), Bellville South - Peters 138 kV, Singleton - Zenith 345 kV (99), Singleton - Tomball 345 kV (74) | RT, ST | Planned, Forced
CNP | Singleton - Zenith (SNGZEN99) | LN | 345 | 15/12, 17/2, 17/3, 17/4, 17/1, 17/5, 17/10, 18/1 | DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 kV, DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 kV, Kuykendahl to Rothwood 345 kV | Singleton - Zenith 345 kV (98), Bellville South - Peters 138 kV, Singleton - Zenith 345 kV (98), Singleton - Tomball 345 kV (74) | RT, ST | Planned
CNP | South Channel - Sr Bertron | LN | 69 | 17/8 | DCKT Cedar Bayou Plant to Strang & Cedar Bayou Plant to Quanum 138 kV, Meadow to Oasis 345 kV, Meadow to Ph Robinson 345 kV | Exxon to Lynch 138 kV, Angleton - Liverpool 138 kV, Seminole Tnp - Friendswood Tnp 138 kV | RT | Planned
CNP | South Lane City - New Gulf | LN | 138 | 15/12 | DCKT Wharton to East Bernard & Dyann 138 kV (UNSOLVED) | N/A | ST | Planned
CNP | Texwal Switchrack - Wallisville | LN | 69 | 17/8 | DCKT Mining to Deepwater & South Channel & Deepwater to Sr Bertron 69 kV | Genral - University 69 kV | RT | Forced
CNP | Village Creek - Zenith | LN | 138 | 18/3 | DCKT Jewett to Singleton 345 kV | Btu Jack Creek - Twin Oak Sw 345 kV; | RT | Planned
CNP | Wa Parish - … - Telview & Dewalt (SIEWAP02) | LN | 138 | 18/4 | DCKT Jewett to Singleton 345 kV | Btu Jack Creek - Twin Oak Sw 345 kV; | RT | Planned
CNP | Webster - Friendswood (FW_WEB05) | LN | 138 | 18/2 | DCKT Jewett to Singleton 345 kV | Btu Jack Creek - Twin Oak Sw 345 kV | RT | Planned
CNP | White Oak Auto AT3 345/138 kV | XF | 345 | 16/6 | DCKT Britmoore to Sauer 138 kV | Bellaire - San Felipe 138 kV | RT | Planned
CNP, CPS | South Texas Project - Elm Creek (STPELM18) | LN | 345 | 16/4 | DCKT Marion to Clear Springs & Zorn 345 kV | Comal - Henne 138 kV | ST | Planned
CNP, CPS | South Texas Project - Elm Creek (STPELM27) | LN | 345 | 16/4 | DCKT Marion to Clear Springs & Zorn 345 kV | Comal - Henne 138 kV | ST | Planned
CNP, STEC | Franklins Camp Sub - … - Jones Creek | LN | 138 | 18/1 | DCKT Jewett to Singleton 345 kV | Btu Jack Creek - Twin Oak Sw 345 kV | RT | Forced |  | Doug Evans | See Frank Camp-Jones Crk tab
CNP, TMPA | Gibbons Creek - Limestone (Gib_Lime18) | LN | 345 | 18/2, 18/3 | DCKT Jewett to Singleton 345 kV | Btu Jack Creek - Twin Oak Sw 345 kV | RT | Planned
CNP, TMPA | Gibbons Creek - Limestone (Gib_Lime50) | LN | 345 | 18/2, 18/3 | DCKT Jewett to Singleton 345 kV | Btu Jack Creek - Twin Oak Sw 345 kV | RT | Planned
CNP, TMPA | Gibbons Creek - Singleton (SNGXGC99) | LN | 345 | 15/12, 17/4, 17/1 | DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 kV, DCKT Jewett to Singleton 345 kV | Singleton - Zenith 345 kV (98), Singleton - Zenith 345 kV (99), Singleton - Gibbons Creek 345 kV (75), Singleton - Gibbons Creek 345 kV (75), Sandow Sw - Bell County East Sw (421) | RT, ST | Planned | Y
CNP, TMPA | Gibbons Creek Bus 5200 (CB 5030, etc.) | BUS | 345 | 17/3 | DCKT Jewett to Singleton 345 kV | Singleton - Gibbons Creek 345 kV (75) | ST | Planned
CNP, TMPA | Singleton - Gibbons Creek (SNGXGC75) | LN | 345 | 17/1, 17/4, 17/11 | DCKT Jewett to Singleton 345 kV | Gibbons Creek - Singleton 345 kV, Singleton - Gibbons Creek 345 kV (99), Singleton - Gibbons Creek 345 kV (99), Sandow Sw - Bell County East Sw (421) | RT, ST | Planned
CNP, TNMP | Ph Robinson - Gaf Tnp | LN | 138 | 18/1 | Caddo Sw Sta Tnp to Greenbelt Tnp 138 kV | Tejas Tnp - Comanche Sw Tnp 138 kV | RT | Planned
CPS | Ballpark - … - Olmos | LN | 138 | 15/5 | DCKT Calaveras to Walzem & Skyline 138 kV | Ball Park - Fern 138 kV | RT | Planned
CPS | Cagnon Auto MR3 | XF | 345 | 15/6 | Cagnon Auto MR1 345/138 kV | Cagnon Auto MR4 345/138 kV | ST | Planned | Y
CPS | Calaveras - Cagnon | LN | 345 | 17/8 | DCKT Calaveras to Skyline 345 kV | Braunig - Cagnon 345 kV | RT | Forced
CPS | Calaveras - Pawnee Switching Station | LN | 345 | 17/8 | DCKT Calaveras to Skyline 345 kV | Braunig - Cagnon 345 kV | RT | Forced
CPS | Calaveras - Skyline (N5_P4) | LN | 345 | 17/5, 17/12 | DCKT Cagnon to Braunig & Calaveras to Cagnon 345 kV, DCKT Hill Country to Marion 345 kV | Skyline - Calaveras 345 kV, Pawnee Switching Station - Calaveras 345 kV, Skyline - Elmcreek 345 kV | RT | Planned, Forced
CPS | Calaveras - Skyline (N5_P4_2) | LN | 345 | 17/12 | DCKT Cagnon to Braunig & Calaveras to Cagnon 345 kV, DCKT Hill Country to Marion 345 kV | Pawnee Switching Station - Calaveras 345 kV, Pawnee Switching Station Auto XF1 345/138 kV, Skyline - Elmcreek 345 kV | RT | Planned
CPS | Cibolocr - ... - Green_Mt | LN | 138 | 15/2 | DCKT Hill Country to Marion & Elmcreek 345 kV | Marion - Skyline 345 kV | RT | Planned
CPS | Elmcreek - Hill Country | LN | 345 | 15/10 | DCKT Marion to Hill Country & Skyline 345 kV | EC Mornhinweg - Parkway Lcra 138 kV | ST | Planned
CPS | Hill Country Bus #1 (CB 11T4, etc.) | BUS | 138 | 15/6 | Cagnon Auto MR1 345/138 kV | Cagnon Auto MR4 345/138 kV | ST | Planned | Y
CPS | Holbrook - Kirby 138 kV | LN | 138 | 16/10 | DCKT Calaveras to Hotwells & Laredo1 138 kV | Kirby - St_Hedwg 138 kV | RT | Planned
CPS | Howard - Somerset | LN | 138 | 17/12, 18/1 | DCKT Castrvll to Razorbac & Txresrch 138kV | Hondo Creek Switching Station - Moore Switching Station 138 kV | RT | Planned
CPS | Laredo 1 - Five Pts | LN | 138 | 15/5 | DCKT Calaveras to Walzem & Skyline 138 kV | Ball Park - Fern 138 kV | RT | Planned
CPS | Nacdches - Wb Tuttle | LN | 138 | 17/1 | DCKT Cagnon to Tcc & Pinn_Rd 138 kV | Medinabs - 36Th Street 138 kV | ST | Planned
CPS | Skyline - Elmcreek (P4_E5_1) | LN | 345 | 16/11 | DCKT Hill Country to Marion & Elmcreek 345 kV | Cibolo - Schertz 138 kV | RT | Planned
CPS | Skyline - Elmcreek (P4_E5_2) | LN | 345 | 16/11, 17/12 | DCKT Hill Country to Marion & Elmcreek 345 kV | Cibolo - Schertz 138 kV, Skyline - Elmcreek 345 kV | RT | Planned
CPS | Txresrch (V3) - Castrvll (D1) | LN | 138 | 16/8, 16/10 | Somerset to Howard 138 kV | Pleasanton Sub - Tordillo 69 kV | ST | Planned | Y
CPS | Weiderstein - Randolph | LN | 138 | 15/9 | DCKT Skyline to Harmony & Nachches 138 kV | Fratt - Parkway Lcra 138 kV | ST | Planned | Y
CROSS | Gray South Bus (CB G130, etc.) | BUS | 345 | 16/5 | DCKT Alibates to Tule Canyon 345 kV | Low Voltage in Panhandle area | ST | Planned | Y
CROSS | Railhead - Gray | LN | 345 | 16/3, 16/5 | Panhandle GTC, Panhandle GTC, DCKT Alibates to Tule Canyon 345 kV | N/A, N/A, Low Voltage in Panhandle area | RT, ST | Planned | Y
CROSS, SHARYLAND | Alibates - Gray | LN | 345 | 16/3, 16/5 | Panhandle GTC, DCKT Alibates to Tule Canyon 345 kV | N/A, Low Voltage in Panhandle area | ST | Planned | Y
DME | Cooper Creek Sub - Industrial Sub | LN | 138 | 15/7 | Lewisville Sw Auto FMR2 345/138 kV | Pockrus Sub - Teasely Sub 138 kV | ST | Planned
DME | Denton Steam - … - Woodrow Substation | LN | 138 | 18/3, 18/4 | DCKT Carrollton Northwest to Lewisville Sw 345 kV, Jones Street Tnp to Lewisville Sw 138 kV | Carrollton Northwest - Lakepointe Tnp 138 kV, Ti Tnp - West Tnp 138 kV | RT | Planned
DME | Teasley - Forth Worth | LN | 138 | 15/10 | Denton Arco to North Denton Interchange 138 kV | Hickory - Locust 69 kV | ST | Planned
DME, GAR | Denton Steam Auto AT1 138/69 kV | XF | 138 | 18/4 | Jones Street Tnp to Lewisville Sw 138 kV | Ti Tnp - West Tnp 138 kV | RT | Planned
DME, ONCOR, TNMP | Arco - Krugerville | LN | 138 | 17/5 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned
DME, TMPA | Arco To - Cooper Creek Sub | LN | 138 | 18/2 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned
DME, TMPA | Cooper Creek Sub - … - Denton Arco | LN | 138 | 15/7 | Lewisville Sw Auto FMR2 345/138 kV | Pockrus Sub - Teasely Sub 138 kV | ST | Planned
DME, TMPA | Fort Worth Sub - West Denton | LN | 138 | 16/10 | DCKT Lewisville Sw to Krum West Sw & Roanoke Sw 345 kV | Jim Christal Sub - West Denton 138 kV | ST | Planned | Y
DME, TMPA | North Denton - Arco - Denton Arco | LN | 138 | 15/7, 16/4, 16/5 | DCKT Lewisville Sw to Krum West Sw & Roanoke Sw 345 kV, DCKT Roanoke Sw to West Denton & Lewisville Sw to Krum West Sw 345 kV | Teasley Sub - Pockrus Sub 138 k, Fort Worth Sub - West Denton 138 kV | RT | Planned, Forced
DME, TMPA | West Denton - Jimchristal | LN | 138 | 18/1 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest to Lakepointe Tnp 138 kV | RT | Planned
ETT, ONCOR | Riley - Krum West Sw (SKRWRI15) | LN | 345 | 17/5 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Blue Mound - Wagley Robertson 138 kV | RT | Forced
ETT, ONCOR | Riley - Krum West Sw (SKRWRI25) | LN | 345 | 17/5 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Blue Mound - Wagley Robertson 138 kV | RT | Forced
GAR | Elmgrove - … - Olinger | LN | 138 | 15/9 | Pruitt to Swindell 138 kV | Ben Davis - Olinger 138 kV | ST | Planned
GAR | Elmgrove - Wylie Sw | LN | 138 | 16/9 | Pruitt to Swindell 138 kV | Ben Davis - Olinger 138 kV | ST | Planned
GAR | Wylie Sw - Olinger (WYL_OLI1) | LN | 138 | 16/4 | Greenville Steam to Shelby 138 kV | Shelby Auto BT1 138/69 kV | ST | Forced
GAR | Wylie Sw - Olinger (WYL_OLI2) | LN | 138 | 15/9, 16/9 | Pruitt to Swindell 138 kV | Ben Davis - Olinger 138 kV | ST | Planned
GAR | Wylie Sw - Olinger (WYL_OLI3) | LN | 138 | 16/9 | Pruitt to Swindell 138 kV | Ben Davis - Olinger 138 kV | ST | Planned
GEUS, TMPA | Diesel - Greenville Steam | LN | 69 | 15/7 | Shelby Auto BT1 138/69 kV | Greenville Steam Auto XT1 138/69 kV | ST | Planned
LCRA | Bevo Auto BEVO | XF | 138 | 15/6 | Bevo Sub to Asherton 138 kV | Hamilton Road - Maverick 138 kV | RT | Planned
LCRA | Clear Springs - Marion | LN | 345 | 18/2, 18/4 | DCKT Kendall to Cagnon 345 kV & Menger Creek to Ranchtwn 138 kV, Kendall to Cagnon 345 kV | CICO - Comfort 138 kV, Marion Auto AT2H 345/138 kV | RT | Planned
LCRA | Coronado - … - Sherwood Shores | LN | 138 | 17/11 | DCKT Granite Mountain to Ferguson & Starcke to Wirtz 138 kV | Burnet Auto AT3L 138/69 kV | RT | Planned
LCRA | Ctec Buchanan - … - Kingsland 1 | LN | 69 | 17/11 | DCKT Granite Mountain to Ferguson & Starcke to Wirtz 138 kV | Burnet Auto AT3L 138/69 kV | RT | Planned
LCRA | Fayette Plant 1 - Fayette Plant 2 | LN | 345 | 15/3, 16/4 | DCKT Lost Pines Aen to Austrop & Aen Dunlap 345 kV | Fayetteville Auto AT2 345/138 kV | ST | Planned
LCRA | Fayette Plant 1 - Fayetteville | LN | 345 | 15/2, 15/3 | DCKT Lost Pines to Austrop & Dunlop 345 kV | Fayette Plant 1 - Fayette Plant 2 345 kV | RT | Planned
LCRA | Fayette Plant 1 - Salem Lcra | LN | 345 | 17/4 | DCKT Lost Pines Aen to Austrop & Aen Dunlap 345 kV | Fayetteville Auto AT2 345/138 kV | ST | Planned
LCRA | Lampasas - … - San Saba | LN | 138 | 17/5 | Comanche Sw (Oncor) to Mercers Gap Sw | Holder Auto FMR1 138/69 kV | RT | Planned
LCRA | Marion - Zorn | LN | 345 | 16/3, 18/2, 18/4 | DCKT South Texas Project Unit 1 & 2, DCKT Kendall to Cagnon 345 kV & Menger Creek to Ranchtwn 138 kV, Kendall to Cagnon 345 kV | Marion - Clear Springs 345 kV, Marion Auto AT2H 345/138 kV, CICO to Comfort 138 kV | RT | Planned
LCRA | Marion Bus #5201 (CB GCB_7010_CB, etc.) | BUS | 345 | 17/12 | DCKT Cagnon to Braunig & Calaveras to Cagnon 345 kV, Clear Springs Auto Trx Cleasp_At1 345/138 kV, DCKT Schertz to Cibolo 138 kV, DCKT Jewett to Singleton 345 kV, Clear Springs to Freiheit 138 kV | Skyline - Elmcreek 345 kV, Clear Springs Auto AT2H 345/138 kV, E C Mornhinweg to Parkway 138 kV, Btu Jack Creek - Twin Oak Sw 345 kV, Henne - Zorn 138 kV | RT | Forced
LCRA | Marion Bus #5202 (CB GCB_7030_CB, etc.) | BUS | 345 | 17/12 | DCKT Cagnon to Braunig & Calaveras to Cagnon 345 kV, Clear Springs Auto Trx Cleasp_At1 345/138 kV, DCKT Schertz to Cibolo 138 kV, DCKT Jewett to Singleton 345 kV, Clear Springs to Freiheit 138 kV | Skyline - Elmcreek 345 kV, Clear Springs Auto AT2H 345/138 kV, E C Mornhinweg - Parkway 138 kV, Btu Jack Creek - Twin Oak Sw 345 kV, Henne - Zorn 138 kV | RT | Forced
LCRA | McElmurray Tap Sw DSC MOS_19119 | DSC | 138 | 16/5 | Sweetwater Downtown to Haynes Sub 138 kV | Eskota Sw - Trent 69 kV | ST | Planned
LCRA | Moore Lcra DSC MOS_13021 | DSC | 138 | 16/5 | Sweetwater Downtown to Haynes Sub 138 kV | Eskota Sw - Trent 69 kV | ST | Planned
LCRA | Pitsburg - … - Ctec Buchanan | LN | 69 | 17/11 | DCKT Granite Mountain to Ferguson & Starcke to Wirtz 138 kV | Burnet Auto AT3L 138/69 kV | RT | Planned
LCRA | Smithville - Winchester | LN | 138 | 17/5 | DCKT Fayetteville Plant 1 to Fayetteville & Fayette Plant 1 to Salem 345 kV | Sam Gideon - Winchester 138 kV | RT | Planned
LCRA | Turnersville - Lytton Springs | LN | 138 | 17/11 | DCKT Stoney Ridge to Garfield Aen & Hicross Aen to Garfield Aen 138 kV | Lytton Springs - Pilot Knob 138 kV | RT | Planned
LCRA | Winchester - Paige | LN | 138 | 17/5 | DCKT Fayetteville Plant 1 to Fayetteville & Fayette Plant 1 to Salem 345 kV | Sam Gideon - Winchester 138 kV | RT | Planned
LCRA | York Creek - Seguin | LN | 138 | 15/9 | DCKT Zorn to Marion & Clear Springs 345 kV | Comal - Henne 138 kV | ST | Forced
LCRA, STEC | Ricebird - Nada | LN | 138 | 18/1 | Dyann to Wharton 138 kV | El_Campo - Lane City Pump 138 kV | RT | Forced
LST, ONCOR | Big Brown Ses - Navarro (10) | LN | 345 | 17/2, 17/4 | DCKT Big Brown Ses to Jewett 345 kV, DCKT Trinidad Ses to Richland Chambers 345 kV | Trinidad Ses - Richland Chambers 345 kV, Big Brown Ses - Jewett 345 kV | RT | Planned
LST, ONCOR | Big Brown Ses - Navarro (60) | LN | 345 | 17/2, 17/4 | DCKT Big Brown Ses to Jewett 345 kV, DCKT Trinidad Ses to Richland Chambers 345 kV, DCKT Limestone to Navarro 345 kV | Trinidad Ses - Richland Chambers 345 kV, Big Brown Ses - Jewett 345 kV | RT, ST | Planned
ONCOR | Alcon Tap - Everman Sw | LN | 138 | 18/4 | DCKT Venus Sw to Everman Sw 345 kV | Oakhill Tap 2 - Tate Tap East 138 kV | RT | Planned
ONCOR | Allen Sw - Renner Sw | LN | 345 | 18/4 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned
ONCOR | Andrews County South - … - Andrews North | LN | 138 | 17/9 | Yucca Drive Sw to Wolf Switching Station 138 kV | No Trees Sw - Cheyenne Tap 138 kV | RT | Forced
ONCOR | Andrews North - Andrews County South | LN | 138 | 17/9 | Yucca Drive Sw to Wolf Switching Station 138 kV | Andrews County South - Amoco Three Bar Tap 138 kV, No Trees Sw - Cheyenne Tap 138 kV | RT | Planned
ONCOR | Audelia Termination - … - Judd Court & Kirkland Park (3250_C) | LN | 138 | 18/2 | DCKT Carrollton Northwest to Lewisville Sw 345 Kv | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned
ONCOR | Benbrook Sw - Parker Sw (6005) | LN | 345 | 18/3 | DCKT Everman Sw to Johnson Sw (Oncor) 345 kV | Parker Sw - Benbrook Sw 345 kV | RT | Planned
ONCOR | Benbrook Sw - Sycamore Creek | LN | 345 | 17/2, 17/3 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV, Lewisville Sw - Jones Street Tnp 138 kV | RT | Forced
ONCOR | Big Brown Ses - Jewett (50) | LN | 345 | 17/4 | DCKT Trinidad Ses to Richland Chambers 345 kV | Big Brown Ses - Jewett 345 kV | RT | Forced
ONCOR | Bowen - … - Bowen Tate Tap & Village Creek | LN | 138 | 17/10 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 Kv | Blue Mound - Wagley Robertson 138 kV | RT | Planned
ONCOR | Brownwood - … - Brownwood Sw | LN | 138 | 17/2, 17/3, 17/4, 17/5 | Mercers Gap Sw to Comanche Sw (Oncor) 138 kV | Holder Auto FMR1 138/69 kV, Holder Auto FMR1 138/69 kV | RT, ST | Planned
ONCOR | Calmont Sw - … - Eagle Mountain Ses (6185) | LN | 138 | 17/4, 18/2 | DCKT Eagle Mountain to Saginaw Sw 138 kV | Eagle Mountain Ses - Morris Dido 138 kV (6265), Eagle Mountain Ses - Eagle Mountain Compressor 138 kV | RT | Planned
ONCOR | Calmont Sw - … - Eagle Mountain Ses (6190) | LN | 138 | 15/6, 15/7, 17/4 | DCKT Eagle Mountain SES to Parker Sw & Hicks Sw 345 kV, DCKT Eagle Mountain SES to Parker Sw & Hicks Sw 345 kv, DCKT Eagle Mountain to Saginaw Sw 138 kV | Calmont Sw - … - Eagle Mountain Ses (6185), Calmont Sw - … - Eagle Mountain Ses (6190), Eagle Mountain Ses - Morris Dido 138 kV (6265) | RT | Planned, Forced
ONCOR | Carrollton Northwest - … - Plano Tennyson (840) | LN | 138 | 16/1, 16/6 | DCKT Carrollton Northwest to Lewisville Sw 345 kV, Lewisville Sw Auto FMR2 345/138 kV | Carrollton Northwest - Lakepointe Tnp 138 kV, Fort Worth Sub - West Denton 138 kV | RT | Planned
ONCOR | Carrollton Northwest Bus #1 | BUS | 345 | 17/4 | Jones Street Tnp to Lewisville Sw 138 kV | Ti Tnp - West Tnp 138 kV | RT | Planned
ONCOR | Carrollton Tarpley Road - … - Renner Sw | LN | 138 | 17/9 | DCKT Liggett Sw to Venus Sw 345 Kv | Sargent Road - Watermill Sw 345 kV | RT | Planned
ONCOR | Cedar Crest Sw - … - Sargent Road 138 kV | LN | 138 | 16/9 | Mountain Creek Ses Unit Unit8 | Industrial Blvd - Compton Street 138 kV | RT | Planned, Forced
ONCOR | Cedar Hill Sw - Mountain Creek Ses (3200) | LN | 138 | 15/9, 16/10, 16/11, 16/9 | Polk Street to Oak Cliff South 138 KV, Mountain Creek Ses Auto MR1 138/69 kV, DCKT Mountain Creek Ses to Cedar Crest Sw 138 kV, West Levee Sw Auto MR1 345/138 kV, Spur - … - Salt Creek Bepc, Polk Street to Oak Cliff South 138 kV | Cedar Crest Sw - Oak Cliff South 138 kV, Irving Hunter Ferrell Tap 2 - Trinity River Authority 138 kV, Industrial Blvd - Compton Street 138 kV, Cedar Crest Sw - Oak Cliff South 138 kV | RT, ST | Planned, Forced
ONCOR | Cedar Hill Sw - Mountain Creek Ses (3210) | LN | 138 | 15/9, 16/10, 16/11, 16/9 | Polk Street to Oak Cliff South 138 KV, Mountain Creek Ses Auto MR1 138/69 kV, DCKT Mountain Creek Ses to Cedar Crest Sw 138 kV, West Levee Sw Auto MR1 345/138 kV, Polk Street to Oak Cliff South 138 kV | Cedar Crest Sw - Oak Cliff South 138 kV, Irving Hunter Ferrell Tap 2 - Trinity River Authority 138 kV, Industrial Blvd - Compton Street 138 kV, Cedar Crest Sw - Oak Cliff South 138 kV | RT, ST | Planned, Forced
ONCOR | Centerville Road Sw - … - Parkdale Sw (3680_C) | LN | 138 | 18/1 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned
ONCOR | Centerville Road Sw - Forney Sw | LN | 345 | 2017 | Forney - Royse DCKT | Forney 345/138 auto | ADD
ONCOR | Chambers - King | LN | 345 | 17/9, 17/10, 18/3 | Meadow to Oasis 345 kV, Ph Robinson to Center 345 kV, DCKT Crown to Tanker & Davson to Greens Bayou 138 KV | Angleton - Liverpool 138 kV, Channelview - Lynch 138 kV, Exxon - Lynch 138 kV, Bigvue - Power Systems - Arco Cogen 138 kV | RT | Planned, Forced
ONCOR | Champion Paper Mill Tap - … - Lufkin Sw | LN | 138 | 17/9 | Nacogdoches Se to Mt Enterprise 345 kV | Stryker Creek Ses - Gresham Road Sw 138 kV | RT | Planned
ONCOR | Chocolate Bayou - … - H O Clarke & Karsten & Quail Valley (QV_TV_26) | LN | 138 | 17/10 | Coleto Creek to Victoria 138 kV, DCKT Jewett to Singleton 345 kV, Meadow to Oasis 345 kV, DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 kV | Coleto Creek - Victoria 138 kV, Btu Jack Creek - Twin Oak Sw 345 kV, Intermediate - Southwyck 138 kV, Singleton - Zenith 345 kV | RT | Planned
ONCOR | Collville - … - Norwood Sw | LN | 138 | 17/11 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned
ONCOR | Comanche Peak Ses - Everman Sw | LN | 345 | 2017 | Comanch Peak Ses to Mitchell Bend 345 kV | Comanch Peak Ses - Wolf Hollow 345 Sw 345 kV | ADD
ONCOR | Comanche Peak Ses - Parker Sw (6016) | LN | 345 | 2017 | Comanch Peak Ses to Johnson Sw & Everman Sw 345 kV | Comanch Peak Ses - Wolf Hollow 345 Sw 345 kV | ADD
ONCOR | Comanche Peak Ses - Parker Sw (6062) | LN | 345 | 2017 | Comanch Peak Ses to Johnson Sw & Everman Sw 345 kV | Comanch Peak Ses - Wolf Hollow 345 Sw 345 kV | ADD
ONCOR | Comanche Sw (Oncor) - Brownwood | LN | 138 | 17/11 | Brownwood Sw to Mercers Gap Sw 138 kV, Comanche Sw (Oncor) to Mercers Gap Sw | Has Auto XFM2 138/69 kV | RT | Planned
ONCOR | Crowley - … - Forest Hill Sw | LN | 138 | 17/10 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 Kv | Blue Mound - Wagley Robertson 138 kV | RT | Planned
ONCOR | Culberson Sw - … - Riverton Sw | LN | 138 | 18/4 | Yucca Drive Sw to Wink Sub 138 kV | Andrews County South - Amoco Three Bar Tap 138 kV | RT | Planned, Forced
ONCOR | Cushing Southest Tap - … - Nacogdoches Se | LN | 138 | 17/12 | DCKT Martin Lake Ses to Stryker Creek Ses & Trinidad Ses to Mt Enterprise 345 kV | Herty North Sw - Nacogdoches Se 138 kV | RT | Forced
ONCOR | Denton Tap - … - Saginaw Sw (6402) | LN | 138 | 17/11 | DCKT Eagle Mountain to Saginaw Sw 138 kV | Eagle Mountain Ses - Eagle Mountain Compressor 138 kV | RT | Planned
ONCOR | Desoto Sw - Watermill Sw | LN | 345 | 17/12 | DCKT Desoto Sw to Cedar Hill Sw & Cedar Hill Sw to Watermill Sw 345 kV | Seagoville - Kleberg Tap | RT | Planned
ONCOR | Diboll Southern Pine - … - Lufkin Pershing Tap & Lufkin Hill Street Tap | LN | 138 | 17/9 | Nacogdoches Se to Mt Enterprise 345 Kv | Stryker Creek Ses - Gresham Road Sw 138 kV | RT | Forced
ONCOR | Duval - North Main Sw | LN | 138 | 18/1 | Forest Hill Sw Auto TRX FMR1 138/69 kV | Handley Ses Auto MR1H 138/69 kV | RT | Planned
ONCOR | Eagle Mountain Ses - … - Saginaw Sw (6260) | LN | 138 | 17/4 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Blue Mound - Wagley Robertson 138 kV | RT | Planned
ONCOR | Eagle Mountain Ses - … - Saginaw Sw (6265) | LN | 138 | 17/4, 17/11, 18/2 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV, DCKT Eagle Mountain to Saginaw Sw 138 kV | Blue Mound - Wagley Robertson 138 kV, Eagle Mountain Ses - Eagle Mountain Compressor 138 kV | RT | Planned
ONCOR | East Levee Sw - … - Record Crossing (3415_C) | LN | 138 | 18/1 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned
ONCOR | East Levee Sw - West Netowrk | LN | 138 | 15/5, 15/6 | DCKT West Levee Sw to 800/900 Network 138 kV | East Levee Sw - Reagan Street 138 kV (3410_A) | RT | Planned
ONCOR | Edgemere Term - … - Kirkland Park (3630_B) | LN | 138 | 18/1 | DCKT Carrollton Northwest to Lewisville Sw 345 Kv | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned
ONCOR | Elkton - Forney Sw | LN | 345 | 2017, 17/11 | Trinidad - Enterprise and - Stryker DCKT | Elkton 345/138 kV auto | ADD, RT | Planned
ONCOR | Elkton - Martin Lake Ses | LN | 345 | 2017 | Martin Lake - Styker and - Enterprise DCKT | Martin Lake - Shamburger | ADD
ONCOR | Euless - … - Grapevine Ball Street (1065) | LN | 138 | 17/4 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned
ONCOR | Euless - … - Grapevine Ball Street (745) | LN | 138 | 17/4 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned, Forced
ONCOR | Euless - … - Hackberry (745) | LN | 138 | 16/12, 17/3 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV, Lewisville Sw - Jones Street Tnp 138 kV | RT | Planned
ONCOR | Euless - … - Kimball Ave & McKamy Tap | LN | 138 | 17/5, 17/10 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 Kv | Blue Mound - Wagley Robertson 138 kV | RT | Planned
ONCOR | Euless - … - Liggett Sw | LN | 138 | 17/10 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Wagley Robertson - Summerfield 138 KV | RT | Planned
ONCOR | Euless - … - Roanoke Sw (1065) | LN | 138 | 16/12, 17/1, 17/2, 17/3, 16/10 | DCKT Carrollton Northwest to Lewisville Sw 345 kV, DCKT Martin Lake Ses to Elkton & Tyler Grande 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV, Lewisville Sw - Jones Street Tnp 138 kV, Tyler Northwest - Shamburger Sw 138 kV | RT, ST | Planned
ONCOR | Everman Sw - Oakhill Tap 1 | LN | 138 | 18/4 | DCKT Venus Sw to Everman Sw 345 kV | Oakhill Tap 2 - Tate Tap East 138 kV | RT | Planned
ONCOR | Forney Sw - Royse Sw (200) | LN | 345 | 2017 | Forney Sw - Centerville Road Sw 345 kV | Forney 345/138 kV Auto MR3 | ADD
ONCOR | Forney Sw - Royse Sw (210) | LN | 345 | 2017 | Forney Sw - Centerville Road Sw 345 kV | Forney 345/138 kV Auto MR3 | ADD
ONCOR | Greenville Ave Sw - … - Kirkland Park (3490_B) | LN | 138 | 17/11, 17/12 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Ti Tnp - West Tnp 138 kV | RT | Planned
ONCOR | Hackberry - … - Norwood Sw (100) | LN | 345 | 16/3, 16/7, 17/3 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV, Lewisville Sw - Jones Street Tnp 138 kV | RT | Planned
ONCOR | Handley Ses - Tate Springs (6310_E) | LN | 138 | 17/11 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Wagley Robertson - Summerfield 138 KV | RT | Planned
ONCOR | Handley Ses - White Tap 1 | LN | 138 | 17/8 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 Kv | Blue Mound - Wagley Robertson 138 kV | RT | Forced
ONCOR | Hicks Sw - … - Roanoke Sw (6273_A, 6273_B, 6273_C) | LN | 138 | 17/6 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Blue Mound - Wagley Robertson 138 kV | RT | Planned
ONCOR | Hicks Sw - … - Roanoke Sw (6274_C, 6274_A) | LN | 138 | 17/6 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Blue Mound - Wagley Robertson 138 kV | RT | Planned
ONCOR | Hicks Sw - … - Saginaw Sw | LN | 138 | 17/11 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Wagley Robertson - Summerfield 138 KV | RT | Planned
ONCOR | Hicks Sw - … - Saginaw Sw (6270) | LN | 138 | 16/2, 16/3, 17/1 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV, Rosen Heights to Eagle Mountain Compressor 138 kV | Eagle Mountain Ses - Morris Dido 138 kV, Rosen Heights Tap 2 - Morris Dido 138 kV, Wagley Robertson - Summerfield 138 kV | RT, ST | Planned, Forced
ONCOR | Hicks Sw - … - Saginaw Sw (6271) | LN | 138 | 16/2, 16/3, 16/12, 17/1, 16/1, 16/10 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV, Rosen Heights to Eagle Mountain Compressor 138 kV, Rosen Heights to Eagle Mountain Compressor, DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Eagle Mountain Ses - Morris Dido 138 kV, Rosen Heights Tap 2 - Morris Dido 138 kV, Wagley Robertson - Summerfield 138 kV, Eagle Mountain Ses - Morris Dido 138 kV, Eagle Mountain Poi - Eagle Mountain Ses 138 kV | RT, ST | Planned, Forced
ONCOR | Hicks Sw - Alliance (106) | LN | 345 | 16/4 | Rosen Heights to Eagle Mountain Compressor 138 kV, Eagle Mountain Ses Auto MR1 345/138 kV, DCKT Eagle Mountain Ses to Saginaw Sw 138 kV | Rosen Heights Tap 2 - Morris Dido 138 kV, Eagle Mountain Ses Auto AX2 345/138 kV, Eagle Mountain Ses - Morris Dido 138 kV | RT, ST | Planned | Y
ONCOR | Hicks Sw - Eagle Mountain Ses 138 kV (6276) | LN | 138 | 17/1 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Wagley Robertson - Summerfield 138 kV | RT | Planned
ONCOR | Hicks Sw - Eagle Mountain Ses 138 kV (6277) | LN | 138 | 17/1 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Wagley Robertson - Summerfield 138 kV | RT | Forced
ONCOR | Hicks Sw Bus West (CB 13580, etc.) | BUS | 138 | 16/12, 17/1 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Eagle Mountain Ses - Morris Dido 138 kV, Wagley Robertson - Summerfield 138 kV | RT | Planned
ONCOR | Hicks Sw CB 11615 | LN | 345 | 16/12 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Eagle Mountain Ses - Morris Dido 138 kV, Wagley Robertson - Summerfield 138 kV | RT | Forced
ONCOR | Hutto - … - Round Rock (1660) - … - Georgetown South (1680) 138 kV | LN | 138 | 16/9 | DCKT Temple Sw to Knob Creek Sw 345 kV & Bell County 138 kV | Round Rock - Chief Brady 138 kV | RT | Planned
ONCOR | Jewett Bus #1 (CB 3900, etc.) | BUS | 345 | 16/11 | DCKT Gibbons Creek to Singleton 345 kV | Jewett - Singleton 345 kV (240) | RT, ST | Planned, Forced
ONCOR | Johnson Sw (Oncor) - Comanche Peak Ses | LN | 345 | 17/5, 17/9, 18/4 | Comanche Peak Ses to Mitchell Bend Sw 345 kV | Wolf Hollow 345 Sw - Comanche Peak Ses 345 kV | RT | Planned
ONCOR | Keller Tap - … - Roanoke Sw | LN | 138 | 18/2 | DCKT Eagle Mountain to Saginaw Sw 138 Kv | Eagle Mountain Ses - Eagle Mountain Compressor 138 kV | RT | Planned
ONCOR | Kennedale - Century | LN | 345 | 18/4 | DCKT Venus Sw to Everman Sw 345 kV | Oakhill Tap 2 - Tate Tap East 138 kV | RT | Planned, Forced
ONCOR | Kirkland Park - … - Greenville Ave Sw (3500_C) | LN | 138 | 18/3 | DCKT Everman Sw to Johnson Sw (Oncor) 345 kV | Parker Sw - Benbrook Sw 345 kV | RT | Planned
ONCOR | Lake Creek Ses Bus #1 (CB 2840, etc.) | BUS | 138 | 15/9 | Waco Mm Mars 2 to Robinson 138 KV, Valley South to Anna Sw & Farmersville Sw 345 kV | Elm Mott - Northcrest Tap 138 kV, Pink Hills Pod - Payne Sw 138 kV | RT, ST | Planned
ONCOR | Lufkin South - … - Lufkin Sw (1370) | LN | 138 | 16/7 | Nacogdoches Se to Mt Enterprise 345 kV | Lufkin - Lufkin Sw 138 kV | RT | Planned
ONCOR | Lufkin Sw - … - Nacogdoches Se | LN | 138 | 17/12 | DCKT Martin Lake Ses to Stryker Creek Ses & Trinidad Ses to Mt Enterprise 345 kV | Herty North Sw - Nacogdoches Se 138 kV | RT | Planned
ONCOR | Lufkin Sw - Stryker Creek Ses | LN | 345 | 15/9, 15/10 | Nacogdoches Se to Mt Enterprise 345 kV | Centerville I45 - Pleasant Springs (Hcec) 138 kV | RT | Planned, Forced
ONCOR | Lufkin Sw Auto MR1 | XF | 345 | 15/10 | Nacogdoches Se to Mt Enterprise 345 kV | Centerville I45 - Pleasant Springs (Hcec) 138 kV | RT | Forced
ONCOR | Martin Lake Ses - Mt Enterprise | LN | 345 | 2017 | Martin Lake - Elktion and Tyler Grande DCKT | Martin Lake - Shamburger | ADD
ONCOR | Martin Lake Ses - Styker Creek Ses | LN | 345 | 2017 | DCKT Martin Lake Ses to Elkton & Tyler Grande 345 kV | Martin Lake Ses - Shamburger Sw 345 kV | ADD
ONCOR | Martin Lake Ses - Tyler Grande | LN | 345 | 2017 | DCKT Martin Lake Ses to Styker Creek Ses & Mt Enterprise 345 kV | Martin Lake Ses - Shamburger Sw 345 kV | ADD
ONCOR | Midland County Northwest Sw - High Sky (6463_A) | LN | 138 | 18/4 | DCKT Dermott Sw to Scurry County South Sw 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned
ONCOR | Mitchell Bend Sw - Decordova Ses | LN | 345 | 18/3 | DCKT Everman Sw to Johnson Sw (Oncor) 345 kV | Parker Sw - Benbrook Sw 345 kV | RT | Planned
ONCOR | Montfort Sw - Trinidad Ses | LN | 138 | 17/12 | DCKT Desoto Sw to Cedar Hill Sw & Cedar Hill Sw to Watermill Sw 345 kV | Seagoville - Kleberg Tap | RT | Planned
ONCOR | Monticello Ses - Sulphur Springs Sw | LN | 345 | 16/3 | DCKT Paris Sw to Valley Ses & Valley South 345 kV | Monticello Ses - Sulphur Springs Sw 345 kV | RT | Planned
ONCOR | Moss Sw - Yukon Sw | LN | 138 | 17/9 | Yucca Drive Sw to Wolf Switching Station 138 kV | Andrews County South - Amoco Three Bar Tap 138 kV | RT | Planned
ONCOR | Mountain Creek Ses - … - West Levee Sw (3380) | LN | 138 | 16/10 | Mountain Creek Ses Auto MR1 138/69 kV | Cedar Crest Sw - Oak Cliff South 138 kV | RT | Planned
ONCOR | Mt Enterprise - Trinidad Ses | LN | 345 | 2017 | DCKT Elkton to Forney & Tyler Grande to Tri Corner 345 kV | Elkton 345/138 kV Auto MR3 | ADD
ONCOR | Northaven Sw - Edgemere Term (3630_C) | LN | 138 | 17/11 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned
ONCOR | Norwood Sw - Cedar Hill Sw | LN | 345 | 17/9 | DCKT Liggett Sw to Venus Sw 345 kV | Sargent Road - Watermill Sw 345 kV | RT | Planned
ONCOR | Norwood Sw Auto Mrh1 345/138 kV | XF | 345 | 17/9 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Blue Mound - Wagley Robertson 138 kV | RT | Planned
ONCOR | Norwood Sw Auto Mrh2 345/138 kV | XF | 345 | 17/9 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Blue Mound - Wagley Robertson 138 kV | RT | Planned
ONCOR | Odessa Basin Sw - … - Wink Sub | LN | 69 | 17/3, 17/4, 17/6 | Chevron Has to Wickett & Wink Sub & Wolf Switching Station 138 kV, Yucca Drive Sw to Wink Sub 138 kV, Wink Sub to Wink Tnp 138 kV | Winkler County 6 Tnp - Wickett Tnp 69 kV, Andrews County South - Amoco Three Bar Tap 138 kV, Wink Sub Auto FMR1 138/69 kV, Wink Sub Auto MR2L 138/69 kV | RT | Planned, Forced
ONCOR | Paris Sw – Monticello Ses | LN | 345 | 2017 | DCKT Paris Sw to Valley Ses & Valley South 345 kV | Paris Sw 345/138 kV Auto MR1 | ADD
ONCOR | Paris Sw - Valley Ses | LN | 345 | 2017 | Paris Sw to Monticello Ses 345kV | Paris Sw 345/138 kV Auto MR1 | ADD
ONCOR | Paris Sw - Valley South | LN | 345 | 2017 | Paris Sw to Monticello Ses 345kV | Paris Sw 345/138 kV Auto MR1 | ADD
ONCOR | Paris Sw Bus BB2 (CB 6790, etc.) | BUS | 345 | 2017 | Paris switch – Valley and Valley south 345 kV Dckt | Paris 345/138 kV auto | ADD
ONCOR | Paris Sw CB_8635 | CB | 345 | 2017 | DCKT Paris Sw to Valley Ses & Valley South 345 kV | Paris Sw 345/138 kV Auto MR1 | ADD
ONCOR | Parkdale Sw - … - Prairie Creek Sw | LN | 138 | 18/2, 18/3 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV | RT | Planned
ONCOR | Permian Basin Ses - … - Yucca Drive Sw (6720_G, 6720_I) | LN | 69 | 17/6 | Wink Sub to Wink Tnp 138 kV | Wink Sub Auto FMR1 138/69 kV | RT | Forced
ONCOR | Permian Basin Ses - Wink Sub | LN | 138 | 15/6 | Chevron Has to Wickett Whiting Oil 138 kV | Northward - Wink Sub 69 kV | RT | Planned
ONCOR | Permian Basin Ses Auto Fmr2 138/69 kV | XF | 138 | 17/6 | Winks to Permian Basin Ses, Wink Sub to Wink Tnp 138 kV | Permian Basin Ses Auto MR1H 138/69 kV, Wink Sub Auto FMR1 138/69 kV, Wink Sub Auto MR2L 138/69 kV | RT | Planned
ONCOR | Permian Basin Ses Bus #2 (CB 2460, etc.) | BUS | 138 | 17/4 | Ward Gulf Tap to Wink Sub 138 kV, Chevron Has to Ward Gulf Tap South 138 kV | Permian Basin Ses Auto MR1 138/69 kV | RT, ST | Planned
ONCOR | Roanoke Sw - Hicks Sw | LN | 345 | 16/4 | Rosen Heights to Eagle Mountain Compressor 138 kV, Eagle Mountain Ses Auto MR1 345/138 kV, DCKT Eagle Mountain Ses to Saginaw Sw 138 kV, Rosen Heights to Rosen Heights Tap 2 | Rosen Heights Tap 2 - Morris Dido 138 kV, Eagle Mountain Ses Auto AX2 345/138 kV, Eagle Mountain Ses - Morris Dido 138 kV, Eagle Mountain Ses - Eagle Mountain Compressor 138 kV | RT, ST | Planned | Y
ONCOR | Rocky Creek - Mitchell Bend Sw | LN | 345 | 18/3 | DCKT Everman Sw to Johnson Sw (Oncor) 345 kV | Parker Sw - Benbrook Sw 345 kV | RT | Planned
ONCOR | Royse Sw Auto #1 | XF | 345 | 15/9 | Royse Sw Auto FMR3 345/138 KV | Forney Sw - Forney West 138 kV | RT | Planned
ONCOR | Sandow 5 Ses - Sandow Sw (1726) | LN | 138 | 2017 | Sandow Sw to Sandow Ses 138 kV (1728) | Sandow Ses - Sandow Sw 138 kV (1725) | ADD
ONCOR | Sandow 5 Ses CB_S5360 | CB | 138 | 2017 | Sandow Sw to Sandow Ses 138 kV (1728) | Sandow Ses - Sandow Sw 138 kV (1725) | ADD
ONCOR | Sandow Ses - Sandow Sw (1725) | LN | 138 | 2017 | Sandow Sw to Sandow Ses 138 kV (1728) | Sandow 5 Ses - Sandow Sw 138 kV (1726) | ADD
ONCOR | Sandow Ses CB_5300 | CB | 138 | 2017 | Sandow Ses to Sandow Sw 138 kV (1725) | Sandow 5 Ses - Sandow Sw 138 kV (1726) | ADD
ONCOR | Sandow Ses CB_5320 | CB | 138 | 2017 | Sandow Sw to Sandow Ses 138 kV (1728) | Sandow 5 Ses - Sandow Sw 138 kV (1726) | ADD
ONCOR | Sandow Sw - Austrop (440) | LN | 345 | 2017 | DCKT Sandow Sw to Bell County East Sw | Taylor - Taylor West 138 kV | ADD
ONCOR | Sandow Sw - Austrop (450) | LN | 345 | 2017 | DCKT Sandow Sw to Bell County East Sw | Taylor - Taylor West 138 kV | ADD
ONCOR | Sandow Sw - Bell County East Sw (421) | LN | 345 | 17/2, 17/4 | DCKT Sandow Sw to Austrop 345 kV | Hutto Sw - Taylor West 138 kV | RT, ST | Planned, Forced
ONCOR | Sandow Sw - Bell County East Sw (431) | LN | 345 | 17/2 | DCKT Sandow Sw to Austrop 345 kV | Hutto Sw - Taylor West 138 kV | RT | Forced
ONCOR | Sandow Sw - Sandow Ses (1728) | LN | 138 | 2017 | Sandow Ses to Sandow Sw 138 kV (1725) | Sandow 5 Ses - Sandow Sw 138 kV (1726) | ADD
ONCOR | Sargent Road - West Levee Sw 345 kV | LN | 345 | 16/9 | Mountain Creek Ses Unit Unit8 | Industrial Blvd - Compton Street 138 kV | RT | Planned
ONCOR | Stryker Creek Ses - Trinidad Ses | LN | 345 | 2017 | DCKT Elkton to Forney & Tyler Grande to Tri Corner 345 kV | Elkton 345/138 kV Auto MR3 | ADD
ONCOR | Temple Sw - Bell County East Sw | LN | 345 | 15/3 | Navarro to Watermill Sw 345 kV | Big Brown Ses - Richland Chambers 345 kV | RT | Planned
ONCOR | Three Mile Draw Sw - Orla Southwest Poi | LN | 138 | 18/1 | Fort Stockton Plant to Re Roserock Solar Plant & Solstice 138 kV | Barilla - Fort Stockton Sw 69 kV | RT | Planned
ONCOR | Tri Corner - Tyler Grande | LN | 345 | 2017 | DCKT Trinidad Ses to Stryker Creek Ses & Mt Enterprise 345 kV | Elkton 345/138 kV Auto MR3 | ADD
ONCOR | Trinidad Ses - Watermill Sw | LN | 345 | 17/12 | DCKT Martin Lake Ses to Stryker Creek Ses & Trinidad Ses to Mt Enterprise 345 kV | Herty North Sw - Nacogdoches Se 138 kV | RT | Planned
ONCOR | Trinidad Ses Bus #1 (CB 4020, etc.) | BUS | 345 | 17/2 | DCKT Big Brown Ses to Jewett 345 kV | Trinidad Ses - Richland Chambers 345 kV | RT | Forced
ONCOR | Tyler East - … - Tyler Grande (1770) | LN | 138 | 16/10, 16/7 | DCKT Martin Lake Ses to Elkton & Tyler Grande 345 kV | Tyler Northwest - Shamburger Sw 138 kV | RT, ST | Planned | Y
ONCOR | Watermill Sw - West Levee Sw | LN | 345 | 17/9 | DCKT Liggett Sw to Venus Sw 345 kV, West Levee Sw Auto Trx Wlvee_3_1 345/138 kV | Sargent Road - Watermill Sw 345 kV, Industrial Blvd - Compton Street 138 kV | RT | Planned
ONCOR | White Tap 1 - Trinity | LN | 138 | 17/8 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Blue Mound - Wagley Robertson 138 kV | RT | Forced
ONCOR | Wink Sub - Orbison Tap | LN | 138 | 18/2 | Fort Stockton Plant to Re Roserock Solar Plant & Solstice 138 kV | Barilla - Fort Stockton Sw 69 kV | RT | Planned
ONCOR | Wink Sub - Yucca Drive Sw | LN | 138 | 18/3 | Chevron Has to Wickett & Wink Sub & Wolf Switching Station 138 kV | Winkler County 6 Tnp - Wickett Tnp 69 kV | RT | Planned
ONCOR | Wink Sub Auto Fmr1 138/69 kV | XF | 138 | 17/6 | Wink Sub to Wink Tnp 138 kV | Wink Sub Auto MR2L 138/69 kV | RT | Planned
ONCOR | Wink Sub Bus BBN (CB 12800, etc.) | BUS | 138 | 17/6 | Winks to Permian Basin Ses | Permian Basin Ses Auto MR1H 138/69 kV | RT | Planned
ONCOR | Wolf Switching Station - Ward Gulf Tap | LN | 138 | 18/4 | Yucca Drive Sw to Wink Sub 138 kV | Winkler County 6 Tnp - Wickett Tnp 69 kV, Andrews County South - Amoco Three Bar Tap 138 kV | RT | Planned
ONCOR | Yucca Drive Sw - … - Holt Sw | LN | 138 | 18/4 | Fort Stockton Plant to Re Roserock Solar Plant & Solstice 138 kV | Barilla - Fort Stockton Sw 69 kV, Pig Creek - Solstice 138 kV | RT | Planned
ONCOR, TNMP | Permian Basin Ses - … - Yucca Drive Sw (6920_A, 6710) | LN | 69 | 18/3 | Yucca Drive Sw to Wink Sub 138 kV | Winkler County 6 Tnp - Wickett Tnp 69 kV, Andrews County South - Amoco Three Bar Tap 138 kV | RT | Planned
SHARYLAND | Alibates - Aj Swope Sharyland Utilities | LN | 345 | 17/4 | Panhandle GTC | N/A | ST | Planned
SHARYLAND | Alibates - Tule Canyon (ALIB_TULE_2) | LN | 345 | 17/1 | Panhandle GTC | N/A | RT | Forced
SHARYLAND | Elbow - Bulldog Su | LN | 138 | 16/9 | Moss Sw to Odessa Ehv Sw 345 kV | Trigas Odessa Tap - Odessa Ehv Sw | ST | Planned | Y
SHARYLAND | Grandview Wind Farm - Alibates | LN | 345 | 15/5 | Isolates Generation | N/A | ST | Planned
SHARYLAND | Tule Canyon - White River (TULEC_WHIT_R1) | LN | 345 | 15/11 | Panhandle GTC | N/A | ST | Planned | Y
SHARYLAND | Tule Canyon - White River (TULEC_WHIT_R2) | LN | 345 | 15/11 | Panhandle GTC | N/A | ST | Planned | Y
SHARYLAND | Tule Canyon Bus #1 (CB TCN7100, etc.) | BUS | 345 | 15/6 | Panhandle GTC | N/A | ST | Planned
SHARYLAND | Tule Canyon Bus #2 (CB TCN7102, etc.) | BUS | 345 | 15/6 | Panhandle GTC | N/A | ST | Planned
SHARYLAND | White River - Wett_Cottonwood (WHIT_RV_W_CW1) | LN | 345 | 15/12 | Panhandle GTC | N/A | RT | Planned
SHARYLAND | White River - Wett_Cottonwood (WHIT_RV_W_CW2) | LN | 345 | 15/12 | Panhandle GTC | N/A | RT | Planned
SHARYLAND | Windmill Entire Station | ST | 345 | 16/8 | Basecase | Resource Isolation | ST | Planned | Y
STEC | Calliham Sw - … - San Miguel Sw & San Miguel 69 kV Switchyard | LN | 69 | 17/6, 18/4 | Zorn to Marion 345 kV, DCKT Big Hill to Kendall 345 kV | Marion - Clear Springs 345 kV, Hamilton Road - Maverick 138 kV | RT | Planned |  | Doug Evans | See Calliham Sw-San Miguel tab
STEC | Fowlerton - Tilden 138 Sub | LN | 138 | 18/1 | San Miguel Auto 345_138 kV Switchyards Trx Sanmgl8_3_2 345/138 kV | San Miguel Gen Auto ATBH 345/138 kV | RT | Forced
STEC | Poteet Sub - Oaks Sub | LN | 69 | 17/12, 18/1 | DCKT Castrvll to Razorbac & Txresrch 138kV | Hondo Creek Switching Station - Moore Switching Station 138 Kv | RT | Planned
STEC | Sam Rayburn - Vanderbilt | LN | 138 | 15/10 | Loop 463 to Sam Rayburn 138 kV | Sam Rayurn Swithcing Station Auto 69_2 138/69 kV | ST | Planned
STEC | San Miguel Auto ATA | XF | 345 | 15/3, 16/2 | DCKT Lon Hill to North Edinburg 345 kV & Orange Grove Sw 138 kV, Pawnee Sw to San Miguel 345 kV | Fannin Sub - Victoria 69 kV, San Miguel Auto ATB 345/138 kV | ST | Planned | Y | Doug Evans | Not requesting removal. See San Mig Auto A tab. The Fannin to Victoria line has been rebuilt with higher ratings. If it were just this line we would be requesting removal. The other contingency and overload look possible depending on generation patterns. Regardless of this contingency/overload pair, if the San Miguel Auto B (see next line) is on this list for loss of the Lobo auto and San Miguel A auto then San Miguel Auto A would be on this list for loss of the Lobo auto and the San Miguel B auto.
STEC | San Miguel Auto ATB | XF | 345 | 15/10 | Lobo Auto AT2 345/138 kV | San Miguel Auto ATA 345/138 kV | ST | Planned
STEC | Vanderbilt Sw - Sam Rayburn Sw 138 kV | LN | 138 | 16/1 | Pawnee Sw to Coleto Creek 345 kV | Magruder - Victoria 138 kV | ST | Planned | Y | Doug Evans | See Vand-Rayburn tab
TMPA | Olinger - … - Pruitt | LN | 138 | 15/7 | Basecase | Low Voltage at Pruitt 138 kV | ST | Planned | Y
TNMP | Choctaw Tnp - … - Terminal Tnp | LN | 69 | 17/11 | DCKT Jewett to Singleton 345 kV | Btu Jack Creek - Twin Oak Sw 345 kV | RT | Planned
TNMP | Dickinson - Freeway Park | LN | 138 | 15/8 | North Alvin Tnp to Meadow 138 KV | PH Robinson - Southshore TNP 138 kV | RT | Forced
TNMP | Freeway Park Tnp - Alvin Tnp | LN | 138 | 16/6, 16/8 | Ph Robinson Auto AT1 345/138 kV, Ph Robinson Auto AT1 345/138 kV, North Alvin Tnp to Meadow 138 kV | Seminole Tnp - Friendswood Tnp 138 kV, Seminole Tnp - Friendswood Tnp 138 kV, Southshore Tnp - Ph Robinson 138 kV | RT, ST | Planned | Y, N
TNMP | Gaf - Greenbelt | LN | 138 | 16/2 | Freeway Park Tnp to Heights Tnp 138 kV | Heights Tnp - Ph Robinson 138 kV | ST | Planned
TNMP | Grant Avenue Tnp - Amoco Tnp | LN | 69 | 17/10, 17/11 | DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 kV, Caddo Sw Sta Tnp to Apache Tnp 138 kV | Singleton - Zenith 345 kV, Choctaw Tap Tnp - Choctaw Tnp | RT | Planned, Forced
TNMP | Greenbelt - Amoco Oil Cogen (G138_23) | LN | 138 | 16/2 | Greenbelt to Caddo Sw 138 kV | Greenbelt - Tejas 138 kV | ST | Planned
TNMP | Ih 20 Tnp Auto Iht1 138/69 kV | XF | 138 | 18/3, 18/4 | Chevron Has to Wickett & Wink Sub & Wolf Switching Station 138 kV, Yucca Drive Sw to Wink Sub 138 kV | Winkler County 6 Tnp - Wickett Tnp 69 kV, Andrews County South - Amoco Three Bar Tap 138 kV | RT | Planned, Forced
TNMP | Jones Street Tnp - Lakepointe Tnp | LN | 138 | 17/11, 17/12 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Ti Tnp - West Tnp 138 kV | RT | Planned
TNMP | Mainland Tnp - Freeway Park Tnp | LN | 138 | 17/11 | DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 kV | Singleton - Zenith 345 kV | RT | Planned
TNMP | Praxair Tap Tnp - Grant Avenue Tnp | LN | 69 | 17/10 | DCKT Roans Prairie to Rothwood & Singleton to Tomball 345 kV | Singleton - Zenith 345 kV | RT | Planned
TNMP | Tejas Tnp - Greenbelt Tnp | LN | 138 | 17/11 | Caddo Sw Sta Tnp to Apache Tnp 138 kV | Choctaw Tap Tnp to Choctaw Tnp | RT | Planned

## Loop 463 - Victoria
18 summer peak case-
Base Case has all Rayburn generation on at full output.
BUS 5502 RAYBURN8 138.00 CKT MW MVAR MVA % 1.0200PU 45.29 X--- LOSSES ---X X---- AREA -----X X---- ZONE -----X 5502
140.76KV MW MVAR 13 STEC_TSP 890 STEC
TO 5500 RAYBURN9 69.000 1 48.5 -4.0 48.6 58 1.0000UN 0.17 4.00 13 STEC_TSP 890 STEC
TO 5513 RAYBURNPLNT8138.00 1 -189.6 29.1 191.8 75 0.02 0.14 13 STEC_TSP 890 STEC
TO 5584 VANDERBLTSW8138.00 1 102.6 -7.3 102.8 65 3.76 13.66 13 STEC_TSP 890 STEC
TO 5680 LOOP463SUB8 138.00 1 5.1 -10.8 11.9 7 0.01 0.04 13 STEC_TSP 882 VEC
TO 5730 FORCORNERSB8138.00 1 33.5 -7.0 34.2 16 0.02 0.12 13 STEC_TSP 882 VEC
Open Four Corners to Rayburn
BUS 5502 RAYBURN8 138.00 CKT MW MVAR MVA % 1.0200PU 46.22 X--- LOSSES ---X X---- AREA -----X X---- ZONE -----X 5502
140.76KV MW MVAR 13 STEC_TSP 890 STEC
TO 5500 RAYBURN9 69.000 1 53.6 -3.8 53.8 64 1.0000UN 0.21 4.88 13 STEC_TSP 890 STEC
TO 5513 RAYBURNPLNT8138.00 1 -189.6 27.9 191.7 75 0.02 0.14 13 STEC_TSP 890 STEC
TO 5584 VANDERBLTSW8138.00 1 108.8 -7.5 109.0 69 4.22 15.36 13 STEC_TSP 890 STEC
TO 5680 LOOP463SUB8 138.00 1 27.2 -16.6 31.9 20 0.07 0.27 13 STEC_TSP 882 VEC
Open Loop 463 – Victoria
BUS 5502 RAYBURN8 138.00 CKT MW MVAR MVA % 1.0200PU 47.55 X--- LOSSES ---X X---- AREA -----X X---- ZONE -----X 5502
140.76KV MW MVAR 13 STEC_TSP 890 STEC
TO 5500 RAYBURN9 69.000 1 59.9 -3.5 60.0 71 1.0000UN 0.26 6.08 13 STEC_TSP 890 STEC
TO 5513 RAYBURNPLNT8138.00 1 -189.6 8.5 189.8 74 0.02 0.14 13 STEC_TSP 890 STEC
TO 5584 VANDERBLTSW8138.00 1 118.7 -7.6 119.0 75 5.03 18.29 13 STEC_TSP 890 STEC
TO 5680 LOOP463SUB8 138.00 1 11.0 2.5 11.3 7 0.01 0.03 13 STEC_TSP 882 VEC
Additional study for likely generation pattern. If both of the Sam Rayburn 69 units are off.
BUS 5502 RAYBURN8 138.00 CKT MW MVAR MVA % 1.0200PU 46.11 X--- LOSSES ---X X---- AREA -----X X---- ZONE -----X 5502
140.76KV MW MVAR 13 STEC_TSP 890 STEC
TO 5500 RAYBURN9 69.000 1 66.7 -2.8 66.8 80 1.0000UN 0.32 7.54 13 STEC_TSP 890 STEC
TO 5513 RAYBURNPLNT8138.00 1 -189.6 8.2 189.8 74 0.02 0.14 13 STEC_TSP 890 STEC
TO 5584 VANDERBLTSW8138.00 1 111.9 -7.9 112.1 70 4.47 16.25 13 STEC_TSP 890 STEC
TO 5680 LOOP463SUB8 138.00 1 11.0 2.5 11.3 7 0.01 0.03 13 STEC_TSP 882 VEC
This is still 17 MVA/20% from being overloaded. Something else must have been out or offline in the study in March of 2016. It is hard to see how Loop 463 – Victoria qualifies to be remain the list.

## Vand_Rayburn
18 summer peak case-
Base Case has all Rayburn generation on at full output.
BUS 8172 VICTORIA4A 138.00 CKT MW MVAR MVA % 1.0254PU 45.20 X--- LOSSES ---X X---- AREA -----X X---- ZONE -----X 8172
141.51KV MW MVAR 8 AEP_TCC 620 N REGION
TO 5607 WRBRTN8 138.00 1 5.1 -0.0 5.1 4 0.01 0.02 13 STEC_TSP 890 STEC
TO 5680 LOOP463SUB8 138.00 1 6.0 12.8 14.1 9 0.01 0.04 13 STEC_TSP 882 VEC
TO 8118 EDNA4A 138.00 1 88.1 -1.8 88.1 40 1.27 7.62 8 AEP_TCC 620 N REGION
TO 8125 LOLITA4A 138.00 1 42.9 -1.7 42.9 20 0.34 1.97 8 AEP_TCC 620 N REGION
TO 8143 V_DUPSW4A 138.00 1 65.0 21.0 68.4 32 0.22 1.30 8 AEP_TCC 640 NORTH LI
TO 8143 V_DUPSW4A 138.00 2 65.1 21.0 68.4 32 0.22 1.31 8 AEP_TCC 640 NORTH LI
TO 8162 COLETO4A 138.00 1 -158.4 2.5 158.5 48 1.35 14.16 8 AEP_TCC 620 N REGION
TO 8162 COLETO4A 138.00 2 -163.0 2.7 163.0 50 1.40 14.56 8 AEP_TCC 620 N REGION
TO 8169 VICTORIA2A 69.000 1 82.5 17.1 84.3 45 1.0000UN 0.12 4.99 8 AEP_TCC 620 N REGION
TO 8169 VICTORIA2A 69.000 2 83.5 17.3 85.3 46 1.0000UN 0.13 5.05 8 AEP_TCC 620 N REGION
TO 8194 MAGRUDER4A 138.00 1 167.4 -9.2 167.7 78 0.74 4.16 8 AEP_TCC 620 N REGION
TO 110881 VIC_VICTORG520.000 3 -124.7 -51.3 134.9 67 1.0000LK 30.00LK 0.28 9.14 908 E_AEP_TCC 918 E_VICTORIA
TO 110882 VIC_VICTORG618.000 4 -159.6 -30.5 162.4 85 1.0000LK 30.00LK 0.45 14.76 908 E_AEP_TCC 918 E_VICTORIA
Open Pawnee to Coleto
BUS 8172 VICTORIA4A 138.00 CKT MW MVAR MVA % 1.0254PU 46.66 X--- LOSSES ---X X---- AREA -----X X---- ZONE -----X 8172
141.51KV MW MVAR 8 AEP_TCC 620 N REGION
TO 5607 WRBRTN8 138.00 1 10.8 -2.2 11.0 9 0.03 0.07 13 STEC_TSP 890 STEC
TO 5680 LOOP463SUB8 138.00 1 24.1 7.9 25.3 16 0.03 0.13 13 STEC_TSP 882 VEC
TO 8118 EDNA4A 138.00 1 96.0 -1.1 96.0 43 1.51 9.05 8 AEP_TCC 620 N REGION
TO 8125 LOLITA4A 138.00 1 51.2 -2.1 51.2 24 0.49 2.81 8 AEP_TCC 620 N REGION
TO 8143 V_DUPSW4A 138.00 1 69.8 20.3 72.7 34 0.25 1.47 8 AEP_TCC 640 NORTH LI
TO 8143 V_DUPSW4A 138.00 2 69.9 20.2 72.7 34 0.25 1.47 8 AEP_TCC 640 NORTH LI
TO 8162 COLETO4A 138.00 1 -191.0 8.8 191.2 58 1.96 20.61 8 AEP_TCC 620 N REGION
TO 8162 COLETO4A 138.00 2 -196.4 9.3 196.7 60 2.04 21.20 8 AEP_TCC 620 N REGION
TO 8169 VICTORIA2A 69.000 1 84.9 16.8 86.5 46 1.0000UN 0.13 5.26 8 AEP_TCC 620 N REGION
TO 8169 VICTORIA2A 69.000 2 85.9 17.0 87.6 47 1.0000UN 0.13 5.32 8 AEP_TCC 620 N REGION
TO 8194 MAGRUDER4A 138.00 1 179.2 -8.9 179.4 83 0.84 4.76 8 AEP_TCC 620 N REGION
TO 110881 VIC_VICTORG520.000 3 -124.7 -53.8 135.8 68 1.0000LK 30.00LK 0.29 9.28 908 E_AEP_TCC 918 E_VICTORIA
TO 110882 VIC_VICTORG618.000 4 -159.5 -32.3 162.8 85 1.0000LK 30.00LK 0.45 14.83 908 E_AEP_TCC 918 E_VICTORIA
Open Vanderbilt to Rayburn
BUS 8172 VICTORIA4A 138.00 CKT MW MVAR MVA % 1.0254PU 47.53 X--- LOSSES ---X X---- AREA -----X X---- ZONE -----X 8172
141.51KV MW MVAR 8 AEP_TCC 620 N REGION
TO 5607 WRBRTN8 138.00 1 12.9 -3.0 13.3 11 0.04 0.10 13 STEC_TSP 890 STEC
TO 5680 LOOP463SUB8 138.00 1 -44.5 27.3 52.2 33 0.15 0.54 13 STEC_TSP 882 VEC
TO 8118 EDNA4A 138.00 1 111.9 1.8 111.9 51 2.05 12.31 8 AEP_TCC 620 N REGION
TO 8125 LOLITA4A 138.00 1 62.0 -2.4 62.0 29 0.71 4.12 8 AEP_TCC 620 N REGION
TO 8143 V_DUPSW4A 138.00 1 75.9 19.4 78.3 37 0.29 1.71 8 AEP_TCC 640 NORTH LI
TO 8143 V_DUPSW4A 138.00 2 76.0 19.3 78.4 37 0.29 1.71 8 AEP_TCC 640 NORTH LI
TO 8162 COLETO4A 138.00 1 -183.7 7.3 183.8 56 1.81 19.06 8 AEP_TCC 620 N REGION
TO 8162 COLETO4A 138.00 2 -189.0 7.8 189.1 58 1.89 19.60 8 AEP_TCC 620 N REGION
TO 8169 VICTORIA2A 69.000 1 87.5 16.5 89.0 48 1.0000UN 0.14 5.56 8 AEP_TCC 620 N REGION
TO 8169 VICTORIA2A 69.000 2 88.5 16.7 90.1 48 1.0000UN 0.14 5.63 8 AEP_TCC 620 N REGION
TO 8194 MAGRUDER4A 138.00 1 186.7 -8.6 186.9 86 0.91 5.16 8 AEP_TCC 620 N REGION
TO 110881 VIC_VICTORG520.000 3 -124.7 -62.8 139.6 70 1.0000LK 30.00LK 0.30 9.81 908 E_AEP_TCC 918 E_VICTORIA
TO 110882 VIC_VICTORG618.000 4 -159.5 -39.3 164.3 86 1.0000LK 30.00LK 0.46 15.10 908 E_AEP_TCC 918 E_VICTORIA
This is still 24 MVA/14% from being overloaded. Something else must have been out or offline in the study in January of 2016. It is hard to see how Vanderbilt to Rayburn qualifies to be remain the list. Additionally the flow on Victoria to McGruder can be mitigated by the Thomaston Phase shifting transformer which is the next station past McGruder on that line.

## Frank Camp-Jones Crk
18 summer peak case-
No Contingency
BUS 975 JKCREEK1 345.00 CKT MW MVAR MVA % 1.0279PU 40.51 X--- LOSSES ---X X---- AREA -----X X---- ZONE -----X 975
354.62KV MW MVAR 12 TMPA_TSP 6 TMPA
TO 967 GIBN_CREK_5 345.00 1 544.5 -2.3 544.5 33 1.81 27.42 12 TMPA_TSP 6 TMPA
TO 3400 TWIN_OAK_N5 345.00 1 -705.7 -8.0 705.7 53 3.79 57.53 1 ONCOR_ED 133 O_ROBERTSON
TO 3WNDTR JKCREEK AUTO WND 1 1 161.2 10.3 161.5 27 1.0000RG 0.05 7.41
Open DCKT Jewett to Singleton
BUS 975 JKCREEK1 345.00 CKT MW MVAR MVA % 1.0247PU 41.33 X--- LOSSES ---X X---- AREA -----X X---- ZONE -----X 975
353.51KV MW MVAR 12 TMPA_TSP 6 TMPA
TO 967 GIBN_CREK_5 345.00 1 753.8 -10.0 753.8 46 3.49 52.87 12 TMPA_TSP 6 TMPA
TO 3400 TWIN_OAK_N5 345.00 1 -926.8 0.7 926.8 70 6.58 99.88 1 ONCOR_ED 133 O_ROBERTSON
TO 3WNDTR JKCREEK AUTO WND 1 1 173.0 9.3 173.3 29 1.0000RG 0.06 8.58
Open Franklins Camp to Jones Creek
BUS 975 JKCREEK1 345.00 CKT MW MVAR MVA % 1.0247PU 41.31 X--- LOSSES ---X X---- AREA -----X X---- ZONE -----X 975
353.51KV MW MVAR 12 TMPA_TSP 6 TMPA
TO 967 GIBN_CREK_5 345.00 1 753.4 -10.1 753.5 46 3.48 52.82 12 TMPA_TSP 6 TMPA
TO 3400 TWIN_OAK_N5 345.00 1 -926.5 0.8 926.5 70 6.57 99.80 1 ONCOR_ED 133 O_ROBERTSON
TO 3WNDTR JKCREEK AUTO WND 1 1 173.0 9.3 173.3 29 1.0000RG 0.06 8.58
The shift factor of opening Franklins Camp to Jones Creek is not only too small to be significant, it reduced the flow on Jack Creek to Twin Oak.

## San Mig Auto A
18 summer peak case-
BUS 5736 FANNINSUB9 69.000 CKT MW MVAR MVA % 1.0173PU 39.46 X--- LOSSES ---X X---- AREA -----X X---- ZONE -----X 5736
70.191KV MW MVAR 13 STEC_TSP 882 VEC
TO LOAD-PQ 5.4 0.8 5.5
TO 8169 VICTORIA2A 69.000 1 -19.1 3.6 19.5 50 0.10 0.81 8 AEP_TCC 620 N REGION
TO 8587 GOLIAD2A 69.000 1 13.7 -4.4 14.4 37 0.27 0.42 8 AEP_TCC 620 N REGION
BUS 5901 MIGUEL5 345.00 CKT MW MVAR MVA % 1.0360PU 45.01 X--- LOSSES ---X X---- AREA -----X X---- ZONE -----X 5901
357.42KV MW MVAR 13 STEC_TSP 890 STEC
TO 5133 ELMCREEK 345.00 1 98.8 -2.7 98.9 8 0.37 3.03 5 CPS_TSP 350 CPS
TO 5133 ELMCREEK 345.00 2 98.8 -2.7 98.9 8 0.37 3.03 5 CPS_TSP 350 CPS
TO 5725 PAWNEESW5 345.00 1 -180.4 -13.5 180.9 11 0.28 4.36 13 STEC_TSP 890 STEC
TO 80219 LOBO7A 345.00 1 92.4 -47.6 104.0 8 0.33 4.13 8 AEP_TCC 635 LAREDO
TO 160131 SAN_SANMIGG124.000 1 -390.5 37.9 392.4 91 1.0250LK 0.45 26.22 913 E_STEC_TSP 1091 E_ATASCOSA
TO 3WNDTR SMIGLT1 WND 1 1 140.0 14.7 140.7 47 1.0000LK 0.13 8.96
TO 3WNDTR SMIGLT2 WND 1 2 140.9 14.0 141.6 47 1.0000LK 0.18 9.01
1st outage combination. Open San Miguel- Pawnee
BUS 5736 FANNINSUB9 69.000 CKT MW MVAR MVA % 1.0175PU 39.81 X--- LOSSES ---X X---- AREA -----X X---- ZONE -----X 5736
70.209KV MW MVAR 13 STEC_TSP 882 VEC
TO LOAD-PQ 5.4 0.8 5.5
TO 8169 VICTORIA2A 69.000 1 -19.7 3.8 20.0 52 0.11 0.86 8 AEP_TCC 620 N REGION
TO 8587 GOLIAD2A 69.000 1 14.3 -4.6 15.0 39 0.29 0.46 8 AEP_TCC 620 N REGION
BUS 5901 MIGUEL5 345.00 CKT MW MVAR MVA % 1.0360PU 43.81 X--- LOSSES ---X X---- AREA -----X X---- ZONE -----X 5901
357.42KV MW MVAR 13 STEC_TSP 890 STEC
TO 5133 ELMCREEK 345.00 1 42.8 2.7 42.9 3 0.10 0.83 5 CPS_TSP 350 CPS
TO 5133 ELMCREEK 345.00 2 42.8 2.7 42.9 3 0.10 0.83 5 CPS_TSP 350 CPS
TO 80219 LOBO7A 345.00 1 61.9 -45.3 76.7 6 0.15 1.86 8 AEP_TCC 635 LAREDO
TO 160131 SAN_SANMIGG124.000 1 -390.6 10.7 390.7 91 1.0250LK 0.45 26.00 913 E_STEC_TSP 1091 E_ATASCOSA
TO 3WNDTR SMIGLT1 WND 1 1 121.1 14.8 122.0 41 1.0000LK 0.10 6.74
TO 3WNDTR SMIGLT2 WND 1 2 121.9 14.3 122.8 41 1.0000LK 0.13 6.78
Open San Miguel Auto A
BUS 5736 FANNINSUB9 69.000 CKT MW MVAR MVA % 1.0175PU 39.58 X--- LOSSES ---X X---- AREA -----X X---- ZONE -----X 5736
70.204KV MW MVAR 13 STEC_TSP 882 VEC
TO LOAD-PQ 5.4 0.8 5.5
TO 8169 VICTORIA2A 69.000 1 -20.2 3.9 20.6 53 0.12 0.90 8 AEP_TCC 620 N REGION
TO 8587 GOLIAD2A 69.000 1 14.8 -4.6 15.5 40 0.31 0.49 8 AEP_TCC 620 N REGION
BUS 5901 MIGUEL5 345.00 CKT MW MVAR MVA % 1.0360PU 44.19 X--- LOSSES ---X X---- AREA -----X X---- ZONE -----X 5901
357.42KV MW MVAR 13 STEC_TSP 890 STEC
TO 5133 ELMCREEK 345.00 1 60.9 0.9 60.9 5 0.16 1.34 5 CPS_TSP 350 CPS
TO 5133 ELMCREEK 345.00 2 60.9 0.9 60.9 5 0.16 1.34 5 CPS_TSP 350 CPS
TO 80219 LOBO7A 345.00 1 74.4 -45.9 87.4 6 0.22 2.68 8 AEP_TCC 635 LAREDO
TO 160131 SAN_SANMIGG124.000 1 -390.6 15.3 390.8 91 1.0250LK 0.45 26.02 913 E_STEC_TSP 1091 E_ATASCOSA
TO 3WNDTR SMIGLT2 WND 1 2 194.4 28.9 196.6 66 1.0000LK 0.35 17.37
The change from 41% to 66% is significant enough to see how this could be a HITE.
2nd outage combination Lon Hill- N Edinburg 345 and Lon Hill- Orange Grove 138
BUS 5736 FANNINSUB9 69.000 CKT MW MVAR MVA % 1.0165PU 38.96 X--- LOSSES ---X X---- AREA -----X X---- ZONE -----X 5736
70.138KV MW MVAR 13 STEC_TSP 882 VEC
TO LOAD-PQ 5.4 0.8 5.5
TO 8169 VICTORIA2A 69.000 1 -22.6 4.0 23.0 59 0.15 1.12 8 AEP_TCC 620 N REGION
TO 8587 GOLIAD2A 69.000 1 17.2 -4.7 17.9 46 0.41 0.65 8 AEP_TCC 620 N REGION
BUS 5901 MIGUEL5 345.00 CKT MW MVAR MVA % 1.0360PU 44.65 X--- LOSSES ---X X---- AREA -----X X---- ZONE -----X 5901
357.42KV MW MVAR 13 STEC_TSP 890 STEC
TO 5133 ELMCREEK 345.00 1 91.7 -2.1 91.7 7 0.32 2.65 5 CPS_TSP 350 CPS
TO 5133 ELMCREEK 345.00 2 91.7 -2.1 91.7 7 0.32 2.65 5 CPS_TSP 350 CPS
TO 5725 PAWNEESW5 345.00 1 -212.0 -5.1 212.0 13 0.38 6.03 13 STEC_TSP 890 STEC
TO 80219 LOBO7A 345.00 1 96.4 -44.4 106.1 8 0.36 4.51 8 AEP_TCC 635 LAREDO
TO 160131 SAN_SANMIGG124.000 1 -390.6 10.0 390.7 91 1.0250LK 0.45 26.00 913 E_STEC_TSP 1091 E_ATASCOSA
TO 3WNDTR SMIGLT1 WND 1 1 160.8 22.2 162.4 54 1.0000LK 0.18 11.93
TO 3WNDTR SMIGLT2 WND 1 2 161.9 21.5 163.3 54 1.0000LK 0.24 12.00
Open San Miguel Auto A
BUS 5736 FANNINSUB9 69.000 CKT MW MVAR MVA % 1.0162PU 38.69 X--- LOSSES ---X X---- AREA -----X X---- ZONE -----X 5736
70.119KV MW MVAR 13 STEC_TSP 882 VEC
TO LOAD-PQ 5.4 0.8 5.5
TO 8169 VICTORIA2A 69.000 1 -23.6 4.0 24.0 62 0.16 1.23 8 AEP_TCC 620 N REGION
TO 8587 GOLIAD2A 69.000 1 18.2 -4.8 18.9 49 0.46 0.72 8 AEP_TCC 620 N REGION
BUS 5901 MIGUEL5 345.00 CKT MW MVAR MVA % 1.0360PU 44.91 X--- LOSSES ---X X---- AREA -----X X---- ZONE -----X 5901
357.42KV MW MVAR 13 STEC_TSP 890 STEC
TO 5133 ELMCREEK 345.00 1 104.8 -3.2 104.9 9 0.41 3.38 5 CPS_TSP 350 CPS
TO 5133 ELMCREEK 345.00 2 104.8 -3.2 104.9 9 0.41 3.38 5 CPS_TSP 350 CPS
TO 5725 PAWNEESW5 345.00 1 -180.0 -6.0 180.1 11 0.28 4.35 13 STEC_TSP 890 STEC
TO 80219 LOBO7A 345.00 1 106.8 -44.5 115.7 8 0.45 5.53 8 AEP_TCC 635 LAREDO
TO 160131 SAN_SANMIGG124.000 1 -390.6 13.2 390.8 91 1.0250LK 0.45 26.01 913 E_STEC_TSP 1091 E_ATASCOSA
TO 3WNDTR SMIGLT2 WND 1 2 254.1 43.8 257.8 86 1.0000LK 0.59 29.89
As there is only 1 MVA flow difference on the Fannin to Victoria line, which is 3% of the 38 MVA line rating in the case used, by opening the San Miguel auto, it seems like this would not be on the HITE list because of this contingency. The case 2018 summer case from March 2018 shows the Victoria to Fannin line ratings as 38, 38, 39. These ratings are not current. The new ratings are 61, 67, 241.

## Calliham Sw-San Miguel
18 summer peak case-
BUS 7050 L_CLEASP5_1Y345.00 CKT MW MVAR MVA % 1.0200PU 43.72 X--- LOSSES ---X X---- AREA -----X X---- ZONE -----X 7050
351.91KV MW MVAR 7 LCRA TSC 540 GUADALUPE
TO 5362 RIONOG_1_5 345.00 1 -391.8 -23.5 392.5 33 0.41 3.95 5 CPS_TSP 351 CPS_GENS
TO 5362 RIONOG_1_5 345.00 2 -391.0 -23.7 391.7 33 0.41 3.94 5 CPS_TSP 351 CPS_GENS
TO 7042 L_ZORN__5_1Y345.00 1 139.8 -8.0 140.1 12 0.11 0.89 7 LCRA TSC 540 GUADALUPE
TO 7044 L_MARION5_1Y345.00 1 13.4 -12.2 18.1 2 0.00 0.01 7 LCRA TSC 540 GUADALUPE
TO 7340 L_GILLCR5_1Y345.00 1 216.4 -28.7 218.3 11 1.53 15.73 7 LCRA TSC 581 TRAVIS
TO 3WNDTR AT1 WND 1 2 195.0 54.0 202.3 42 1.0000LK 0.13 13.40
TO 3WNDTR AT2 WND 1 2 218.2 42.1 222.2 46 1.0000LK 0.18 14.52
BUS 8692 MAVERICK4A 138.00 CKT MW MVAR MVA % 1.0128PU 19.11 X--- LOSSES ---X X---- AREA -----X X---- ZONE -----X 8692
139.77KV MW MVAR 8 AEP_TCC 636 TRIANGLE
TO LOAD-PQ 2.9 0.9 3.0
TO 8255 HAMILTON4A 138.00 1 -59.1 14.5 60.8 49 2.43 6.37 8 AEP_TCC 636 TRIANGLE
TO 8264 EAGLHYTP4A 138.00 1 56.2 -15.5 58.3 47 0.13 0.33 8 AEP_TCC 636 TRIANGLE
1st outage combination
open Marion- Zorn
BUS 7050 L_CLEASP5_1Y345.00 CKT MW MVAR MVA % 1.0200PU 43.73 X--- LOSSES ---X X---- AREA -----X X---- ZONE -----X 7050
351.90KV MW MVAR 7 LCRA TSC 540 GUADALUPE
TO 5362 RIONOG_1_5 345.00 1 -391.8 -24.4 392.6 33 0.41 3.95 5 CPS_TSP 351 CPS_GENS
TO 5362 RIONOG_1_5 345.00 2 -391.0 -24.5 391.7 33 0.41 3.95 5 CPS_TSP 351 CPS_GENS
TO 7042 L_ZORN__5_1Y345.00 1 183.6 -11.4 184.0 16 0.18 1.54 7 LCRA TSC 540 GUADALUPE
TO 7044 L_MARION5_1Y345.00 1 -33.5 -7.1 34.2 3 0.01 0.05 7 LCRA TSC 540 GUADALUPE
TO 7340 L_GILLCR5_1Y345.00 1 219.0 -28.7 220.8 11 1.56 16.11 7 LCRA TSC 581 TRAVIS
TO 3WNDTR AT1 WND 1 2 195.2 54.1 202.5 42 1.0000LK 0.13 13.43
TO 3WNDTR AT2 WND 1 2 218.5 42.1 222.5 47 1.0000LK 0.18 14.55
BUS 8692 MAVERICK4A 138.00 CKT MW MVAR MVA % 1.0129PU 19.15 X--- LOSSES ---X X---- AREA -----X X---- ZONE -----X 8692
139.77KV MW MVAR 8 AEP_TCC 636 TRIANGLE
TO LOAD-PQ 2.9 0.9 3.0
TO 8255 HAMILTON4A 138.00 1 -59.0 14.5 60.7 49 2.42 6.35 8 AEP_TCC 636 TRIANGLE
TO 8264 EAGLHYTP4A 138.00 1 56.1 -15.4 58.2 47 0.13 0.33 8 AEP_TCC 636 TRIANGLE
open San Mig Sw to San Mig Tap
BUS 7050 L_CLEASP5_1Y345.00 CKT MW MVAR MVA % 1.0200PU 43.73 X--- LOSSES ---X X---- AREA -----X X---- ZONE -----X 7050
351.90KV MW MVAR 7 LCRA TSC 540 GUADALUPE
TO 5362 RIONOG_1_5 345.00 1 -391.8 -24.4 392.6 33 0.41 3.95 5 CPS_TSP 351 CPS_GENS
TO 5362 RIONOG_1_5 345.00 2 -391.0 -24.6 391.7 33 0.41 3.95 5 CPS_TSP 351 CPS_GENS
TO 7042 L_ZORN__5_1Y345.00 1 184.0 -11.5 184.4 16 0.18 1.54 7 LCRA TSC 540 GUADALUPE
TO 7044 L_MARION5_1Y345.00 1 -34.1 -7.1 34.8 3 0.01 0.05 7 LCRA TSC 540 GUADALUPE
TO 7340 L_GILLCR5_1Y345.00 1 219.0 -28.7 220.9 11 1.56 16.12 7 LCRA TSC 581 TRAVIS
TO 3WNDTR AT1 WND 1 2 195.2 54.1 202.6 42 1.0000LK 0.13 13.44
TO 3WNDTR AT2 WND 1 2 218.5 42.1 222.6 47 1.0000LK 0.18 14.56
BUS 8692 MAVERICK4A 138.00 CKT MW MVAR MVA % 1.0128PU 19.13 X--- LOSSES ---X X---- AREA -----X X---- ZONE -----X 8692
139.76KV MW MVAR 8 AEP_TCC 636 TRIANGLE
TO LOAD-PQ 2.9 0.9 3.0
TO 8255 HAMILTON4A 138.00 1 -59.0 14.4 60.8 49 2.42 6.36 8 AEP_TCC 636 TRIANGLE
TO 8264 EAGLHYTP4A 138.00 1 56.1 -15.4 58.2 47 0.13 0.33 8 AEP_TCC 636 TRIANGLE
Opening the line from San Miguel changed the flows on Clear Spring to Marion by 0.6 MVA. This seems far to low of a shift factor to be used on the HITE list.
2nd outage combination
Open Kendal to Edison DCKT. Did not think it was necessary to also open Edison to Orested and Orested to Big Hill.
BUS 7050 L_CLEASP5_1Y345.00 CKT MW MVAR MVA % 1.0200PU 43.41 X--- LOSSES ---X X---- AREA -----X X---- ZONE -----X 7050
351.91KV MW MVAR 7 LCRA TSC 540 GUADALUPE
TO 5362 RIONOG_1_5 345.00 1 -391.8 -23.5 392.5 33 0.41 3.95 5 CPS_TSP 351 CPS_GENS
TO 5362 RIONOG_1_5 345.00 2 -391.0 -23.7 391.7 33 0.41 3.94 5 CPS_TSP 351 CPS_GENS
TO 7042 L_ZORN__5_1Y345.00 1 139.4 -7.8 139.6 12 0.11 0.88 7 LCRA TSC 540 GUADALUPE
TO 7044 L_MARION5_1Y345.00 1 23.8 -13.4 27.3 2 0.00 0.03 7 LCRA TSC 540 GUADALUPE
TO 7340 L_GILLCR5_1Y345.00 1 204.8 -28.3 206.8 10 1.37 14.10 7 LCRA TSC 581 TRAVIS
TO 3WNDTR AT1 WND 1 2 195.7 54.3 203.1 43 1.0000LK 0.13 13.50
TO 3WNDTR AT2 WND 1 2 219.0 42.4 223.1 47 1.0000LK 0.18 14.63
BUS 8692 MAVERICK4A 138.00 CKT MW MVAR MVA % 1.0127PU 19.16 X--- LOSSES ---X X---- AREA -----X X---- ZONE -----X 8692
139.75KV MW MVAR 8 AEP_TCC 636 TRIANGLE
TO LOAD-PQ 2.9 0.9 3.0
TO 8255 HAMILTON4A 138.00 1 -60.6 15.2 62.5 51 2.56 6.72 8 AEP_TCC 636 TRIANGLE
TO 8264 EAGLHYTP4A 138.00 1 57.7 -16.1 59.9 48 0.13 0.35 8 AEP_TCC 636 TRIANGLE
open San Mig Sw to San Mig Tap
BUS 7050 L_CLEASP5_1Y345.00 CKT MW MVAR MVA % 1.0200PU 43.40 X--- LOSSES ---X X---- AREA -----X X---- ZONE -----X 7050
351.91KV MW MVAR 7 LCRA TSC 540 GUADALUPE
TO 5362 RIONOG_1_5 345.00 1 -391.8 -23.5 392.5 33 0.41 3.95 5 CPS_TSP 351 CPS_GENS
TO 5362 RIONOG_1_5 345.00 2 -391.0 -23.7 391.7 33 0.41 3.94 5 CPS_TSP 351 CPS_GENS
TO 7042 L_ZORN__5_1Y345.00 1 139.6 -7.8 139.8 12 0.11 0.89 7 LCRA TSC 540 GUADALUPE
TO 7044 L_MARION5_1Y345.00 1 23.4 -13.4 27.0 2 0.00 0.03 7 LCRA TSC 540 GUADALUPE
TO 7340 L_GILLCR5_1Y345.00 1 204.9 -28.3 206.9 10 1.37 14.11 7 LCRA TSC 581 TRAVIS
TO 3WNDTR AT1 WND 1 2 195.7 54.3 203.1 43 1.0000LK 0.13 13.51
TO 3WNDTR AT2 WND 1 2 219.1 42.4 223.2 47 1.0000LK 0.18 14.64
BUS 8692 MAVERICK4A 138.00 CKT MW MVAR MVA % 1.0126PU 19.15 X--- LOSSES ---X X---- AREA -----X X---- ZONE -----X 8692
139.73KV MW MVAR 8 AEP_TCC 636 TRIANGLE
TO LOAD-PQ 2.9 0.9 3.0
TO 8255 HAMILTON4A 138.00 1 -60.6 15.2 62.5 51 2.57 6.73 8 AEP_TCC 636 TRIANGLE
TO 8264 EAGLHYTP4A 138.00 1 57.8 -16.1 60.0 49 0.13 0.35 8 AEP_TCC 636 TRIANGLE
Opening the line from San Miguel did not change the flows on Clear Spring to Marion. 0% does not seems like a shift factor that should be used to create the HITE list.